## Helpful Information
Helpful Information
1 | Before completing the template it is best to do an informal interview with the individual in charge of the facilities. This is especially helpful when completing the checklists i.e., ADA, Harmful Substances, etc.
2 | Please ensure that you are interviewing the correct person to complete the checklists. For example, you may need to talk to the Internet Service Provider to complete the IT checklist.
3 | It is recommended that you complete the assessment on-site. Enter percentages and levels of action on-site after the walkthrough and before leaving the facility.
4 | In order for the template to accurately calculate information please complete the "Base Information Sheet." Cells highlighted in yellow are required as the rest of the template will not calculated correctly without that information.
5 | In order for the template to function properly do not change information on the READ ONLY tabs (worksheets e.g., "Building Type Budget-READ ONLY")
6 | It is best to use the template in Microsoft Excel as mobile devices and other application platforms such as Apple will not show the comments. However, a "Physical Assessment Comments" tab is located in the template.
7 | Make sure you hover over the upper right hand corner of cells to view comments. They determine the level of action. Pay attention whether a comment says “and” or “or.”
8 | Use “x” to indicate a system is present.
9 | Use “0” to indicate that a system is not present.
10 | When you are using your expertise to override the built-in cost model document that decision in the "Notes" sections. Notes must be added so the state and districts know why you are overriding the template. Example, a system has a key component that needs to be replaced but that replacement is not accurately described in the "Level of Action" comments.
11 | If you have a system not found in the template then add it at the bottom of the "Physical Condition Assessment."
12 | If you know that costs have changed override the cost on the Physical Condition Assessment tab ONLY and note it.
13 | Please note that some units of measure differ from the gross square footage of the building. The new units of measure are provided as comments in the category description. This is to address some of the concerns with using gross square footage for units that aren't really based on square footage. Example: the percentage of exterior doors that are wood is the number of wood exterior doors divided by the total number of exterior doors. If a school has 10 exterior doors and 7 are wood, then 70% of the doors are wood and that is the percentage that goes into the % of Building column.
14 | Please create a different assessment Excel workbook for each building.
15 | The default for portables is to list them in the Renovations, Additions, & Prtbls tab. If a district requests a full assessment of their portable classrooms, please create a separate assessment Excel workbook for each building.
16 | If an ADA deficiency is listed in the Physical Condition Assessment tab, then include that in the final costs. However, please do not add costs to the final amounts simply to bring building into ADA compliance.
17 | Please remember that this tool is to provide the districts and state with budget level estimates on costs of repairs to buildings. If after reviewing the total costs, including the built in soft cost multiplier, your expert opinion is that the costs are too low, please increase the costs and note it in the "Notes" section.

## Base Information Sheet
Item | Data | Notes / Explanation
District Name: | Lincoln County SD | Pull-down menu of the 197 Districts
Site Name: | Taft Elementary School | Typically the name that is used for the facility / campus
Main
Building Name: | Main | If only one building on site, refer to "main"
Building ID: | N/A | District assigned, but based on State format*
Building Type: | Elementary School | Pull-down menu - feeds RCI calculation
Physical Address of Building: | 4040 SE High School Dr., Lincoln City, OR 97367 | Informational only - does not link
County: | Lincoln | Pull-down menu of the 36 counties - sets location factor for budgets
Gross Square Footage: | 66407 | Calculated from exterior face of walls (excluding eaves, outbuilding, porches, canopies, and similar)
Site Acreage: |  | District records
Assessor Company: | GLAS Architects LLC | Certified company
Assessor Name: | Chris Walkup | For follow up questions
Contact (Phone): | 541.686.2014
Contact (E-Mail): | ChrisWalkup@glas-arch.com
Date of Assessment: |  | Might reference back for inflation calculation (future)
*Building ID Format: Seven (7) digit number with first four digits as the district's Institution ID and last three digits assigned by District for building number

## Physical Condition Assessment
District Name: |  | Lincoln County SD |  |  | REMINDER: FILL OUT ALL INFORMATION ON 'BASE INFORMATION SHEET' BEFORE ENTERING DATA ON THIS SHEET
Site Name: |  | Taft Elementary School |  |  |  | An unused cell or system that should not receive direct user input
Building Name: |  | Main |  |  |  | An automatically populated cell from user input elsewhere in the file - do not overwrite
Building ID: |  | N/A
LEVEL OF ACTION
Level 1 | Level 2 | Level 3 | Type (as applicable) | % of Building |  | None |  | Minor |  | Moderate |  | Major |  | Replace | % of System or Finish | Automated Budget Estimate | Notes
A SUBSTRUCTURE
A10 Foundations
|  | A1010 Standard Foundations |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | A1020 Special Foundations |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | A1030 Slab on Grade |  | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
A20 Basement Construction
|  | A2010 Basement Excavation | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace
|  | A2020 Basement Walls |  | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
B SHELL
B10 Superstructure
|  | B1010 Floor Construction | Wood | 10% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Steel |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Concrete | 90% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | B1020 Roof Construction | Wood | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Steel |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Concrete |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
B20 Exterior Enclosure
|  | B2010 Exterior Walls | Concrete Formed / Tilt | 0% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Masonry | 5% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Framed w/Panel Siding | 90% |  | None |  | Minor | x | Moderate |  | Major |  | Replace | 25% | 98614.395 | Kitchen/Cafeteria area
|  |  | Framed w/Stucco |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Framed w/Masonry Veneer | 5% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | B2020 Exterior Windows | Wood |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Aluminum/Steel |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Clad | 100% |  | None |  | Minor | x | Moderate |  | Major |  | Replace | 10% | 29219.08
|  |  | Curtain Wall |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | B2030 Exterior Doors | Wood |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Hollow Metal | 23 |  | None |  | Minor | x | Moderate |  | Major |  | Replace | 6.5 | 49335
|  |  | Storefront | 1 |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
B30 Roofing
|  | B3010 Roof Coverings | Asphalt Shingle | 15% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Built-Up | 10% |  | None |  | Minor |  | Moderate |  | Major | x | Replace | 150% | 109571.55
|  |  | Single Ply | 75% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Metal |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Concrete Tile |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | B3020 Roof Openings | Skylights | 0 |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Access Hatch | 0 |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
C INTERIORS
C10 Interior Construction
|  | C1010 Partitions | Framed | 95% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Masonry | 5% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | C1020 Interior Doors | Wood | 112 |  | None |  | Minor |  | Moderate |  | Major | x | Replace | 2.5 | 400400
|  |  | Hollow Metal | 5 |  | None |  | Minor |  | Moderate |  | Major | x | Replace | 5 | 30250
|  | C1030 Fittings | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace
C20 Stairs
|  | C2010 Stair Construction | Wood | 0 |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Metal | 0 |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Concrete | 0 |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | C2020 Stair Finishes | Concrete Fill | 0% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Resilient | 0% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
C30 Interior Finishes
|  | C3010 Wall Finishes | Paint on Masonry | 5% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Wallboard | 95% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Wainscot | 20% |  | None |  | Minor |  | Moderate |  | Major | x | Replace | 100% | 175314.48 | Install P-Lam
|  |  | Ceramic Tile | 0% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | C3020 Floor Finishes | Carpet / Soft Surface | 5% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Resilient Tile | 75% |  | None |  | Minor |  | Moderate |  | Major | x | Replace | 40% | 120528.705 | Asbestos abatement and flooring replacement
|  |  | Resilient Sheet |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Polished Concrete |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Ceramic Tile | 5% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Liquid Applied |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Wood Sports Floor | 15% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | C3030 Ceiling Finishes | Wallboard |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Lay-In Ceiling Tile | 20% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Glued-Up Ceiling Tile | 80% |  | None |  | Minor |  | Moderate |  | Major | x | Replace | 50% | 131485.86
|  |  | Painted Structure |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
D SERVICES
D10 Conveying
|  | D1010 Elevators & Lifts |  | 0 |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D1020 Escalators & Moving Walks |  | 0 |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D1090 Other Conveying Systems |  | 0 |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
D20 Plumbing
|  | D2010 Plumbing Fixtures |  | 100% |  | None |  | Minor | x | Moderate |  | Major | x | Replace | 7% | 56246.729 | Restroom replacements
|  | D2020 Domestic Water Distribution |  | 100% |  | None |  | Minor |  | Moderate |  | Major | x | Replace | 140% | 306800.34 | Replace copper plumbing and main meter
|  | D2030 Sanitary Waste |  | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D2040 Rain Water Drainage |  | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D2090 Other Plumbing Systems | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace
D30 HVAC
|  | D3010 Energy Supply |  | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D3020 Heat Generating Systems | Boiler | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Air Handler | 100% |  | None |  | Minor |  | Moderate |  | Major | x | Replace | 100% | 219143.1
|  |  | Furnace | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Heat Exchanger |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D3030 Cooling Generating Systems | Component of air handler |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Stand alone chiller |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D3040 Distribution Systems | Ductwork |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Hot water return & supply | 100% |  | None |  | Minor | x | Moderate |  | Major |  | Replace | 100% | 219143.1 | Replacement of supply & return lines
|  | D3050 Terminal & Package Units | Above ceiling VAV unit |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | In-room ventilator unit | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | In-room radiant unit |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D3060 Controls & Instrumentation |  | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D3070 Systems Testing & Balancing |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D3090 Other HVAC Systems & Equipment | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace
D40 Fire Protection
|  | D4010 Sprinklers |  | 100% |  | None |  | Minor | x | Moderate |  | Major |  | Replace | 70% | 102266.78
|  | D4020 Standpipes |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D4030 Fire Protection Specialties |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D4090 Other Fire Protection Systems | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace
D50 Electrical
|  | D5010 Electrical Service & Distribution |  | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D5020 Lighting and Branch Wiring |  | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D5030 Communications & Security | Voice / Data System | 100% |  | None |  | Minor |  | Moderate |  | Major | x | Replace | 100% | 401762.35 | VOIP
|  |  | Clock / Intercom System | 100% |  | None |  | Minor |  | Moderate | x | Major |  | Replace | 25% | 45654.8125
|  |  | Closed Circuit Surveillance | 100% |  | None |  | Minor |  | Moderate | x | Major |  | Replace | 30% | 14244.3015
|  |  | Access Control System | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Intrusion Alarm System | 0% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Fire Alarm / Detection | 100% |  | None |  | Minor |  | Moderate |  | Major | x | Replace | 40% | 65742.93
|  |  | Lighting Control System | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | D5090 Other Electrical Systems | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace
E EQUIPMENT & FURNISHINGS
E10 Equipment
|  | E1010 Commercial Equipment | Food Service | 100% |  | None |  | Minor | x | Moderate |  | Major |  | Replace | 100% | 47481.005
|  |  | Vocational | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | E1020 Institutional Equipment | Science | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Art | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Stage Performance | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Restroom Accessories/Stalls | 100% |  | None |  | Minor |  | Moderate |  | Major | x | Replace | 2% | 36523.85
|  | E1030 Vehicular Equipment | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace
|  | E1090 Other Equipment | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace
E20 Furnishings
|  | E2010 Fixed Furnishings |  | 100% |  | None |  | Minor |  | Moderate | x | Major |  | Replace | 100% | 438286.2 | Replacement of cabinetry
|  | E2020 Movable Furnishings |  | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
F SPECIAL CONSTRUCTION & DEMOLITION - NOT USED
G BUILDING SITE WORK
| G10 Site Preparation |  | NOT USED
G20 Site Improvements
|  | G2010 Roadways |  | 0 |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | G2020 Parking Lots |  | 76 |  | None | x | Minor |  | Moderate |  | Major |  | Replace | 100% | 250.8 | Seal Coat
|  | G2030 Pedestrian Paving |  | 0 |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | G2040 Site Development |  | 0 |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | G2050 Landscaping |  | 0 |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
G30 Site Mechanical Utilities
|  | G3010 Water Supply | Domestic | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Fire | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | G3020 Sanitary Sewer |  | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | G3030 Storm Sewer |  | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | G3040 Heating Distribution |  | 0% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | G3050 Cooling Distribution |  | 0% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | G3060 Fuel Distribution |  | 0% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | G3090 Other Site Mechanical Utilities | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace
G40 Site Electrical Utilities
|  | G4010 Electrical Distribution | Service | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  |  | Generator | 0% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | G4020 Site Lighting |  | 100% |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | G4030 Site Communications & Security |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  | 0
|  | G4090 Other Site Electrical Utilities | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace
| G90 Other Site Construction |  | NOT USED
OTHER
| Description of System | [8 empty] | Unit of Measure |  | Quantity |  | Unit Budget |  | Extended | Notes
|  | Playground | [7 empty] | 1 |  | 1 |  | 30000 |  | 30000
|  | Covered Play Shed | [7 empty] | 1 |  | 1 |  | 300000 |  | 300000
0
0
0
0
0
[15 empty] | Physical Condition Budget Sub-Total | 3428265.368
[15 empty] | Budgeted Development Costs | 1302740.8398
[15 empty] | Physical Condition Budget TOTAL | 4731006.2078
[15 empty] | Replacement Budget | 27721602.15
[15 empty] | Replacement Cost Index (RCI) | 17.07%
Note on C10: Standard spread and strip / perimeter footings; Apply rates to bldg footprint area
Note on H10: Minor cracking observed - fill and seal the cracks to prevent water intrusion
Note on L10: Settlement observed in surrounding conditions - requiring stabilization of the foundation, sub-grade adjustment, and re-enforcement of the foundation
Note on C11: Pilings or other extended foundation systems that overcome non-standard soil conditions; Apply rates to bldg footprint area
Note on H11: Minor cracking observed - fill and seal the cracks to prevent water intrusion
Note on L11: Settlement observed in surrounding conditions - requiring stabilization of the foundation, sub-grade adjustment, and re-enforcement of the foundation
Note on C12: Standard ground-set concrete slab. If slab is elevated (i.e. has a crawl space or basement), apply conditions to B1010 instead; Apply rates to bldg footprint area
Note on J12: Separation cracks occurring requiring route and fill and patch
Note on L12: Differential settlement occurring - requires removal of section of slab, adjustment to sub-grade, and new infill
Note on C15: Assumed as concrete walls with water-proofing on the exterior. Includes only the structural portion and not the wall finishes; Apply to wall surface area
Note on H15: Inadequate below grade venting is observed - cut in and add venting
Note on J15: Wall is cracked and spalling requiring route and fill and patch and re-finish
Note on L15: Wall is cracked with evidence of water intrusion. Repairs to be implemented and water barrier to be applied to be applied
Note on C18: A suspended floor including the structural members and floor construction, but not including the actual finish
Note on J18: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck
Note on N18: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on J19: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck
Note on N19: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on J20: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck
Note on N20: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on C21: The roof structure referring to the supporting structure and the deck but excluding the roofing itself
Note on L21: Evidence of a spongy decking from water intrusion - replacing the deck but not the trusses
Note on N21: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on L22: Evidence of a flexing decking from water intrusion / rust - replacing the deck but not the trusses
Note on N22: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on L23: Evidence of a spongy / spalling deck from water intrusion - replacing the deck but not the beams
Note on N23: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on D25: Apply to wall surface area
Note on J25: Surface is in tact but finish is deteriorated - paint
Note on L25: Cracks visible - route and patch prior to painting
Note on D26: Apply to wall surface area
Note on J26: Surface is in tact but finish is deteriorated - paint
Note on L26: Some blocks are damaged, needing patch and repair prior to sealing or painting
Note on N26: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on D27: Apply to wall surface area
Note on J27: Surface is in tact but finish is deteriorated - paint
Note on L27: A number of panels are damaged, requiring patch and repair prior to re-painting
Note on N27: The panels are lifting or separating or otherwise losing their integrity - remove and replace
Note on D28: Apply to wall surface area
Note on J28: Surface is in tact but finish is deteriorated - paint
Note on L28: Cracks visible - route and patch prior to painting
Note on N28: System in failure with evidence of water intrusion - remove and replace
Note on D29: Apply to wall surface area
Note on J29: Minor repairs needed to mortar, prep, and re-sealing
Note on L29: Mortar missing in a majority of areas requiring complete re-pointing and sealing
Note on N29: Masonry visibly damaged and requiring removal and replacement
Note on D30: Apply to glazed area
Note on J30: The glazing is double pane but is broken or fogged and requires replacement
Note on L30: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing
Note on N30: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D31: This assumes both individual aluminum windows and storefront systems; Apply to glazed area
Note on J31: The glazing is double pane but is broken or fogged and requires replacement
Note on L31: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing
Note on N31: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D32: This assumes a metal windows system clad with wood or vinyl; Apply to glazed area
Note on J32: The glazing is double pane but is broken or fogged and requires replacement
Note on L32: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing
Note on N32: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D33: Apply to glazed area
Note on J33: Minor leaks at wall seams - re-caulk and re-seal
Note on L33: Window panels fogged and require replacement
Note on N33: Settlement or displacement is evident
Note on D34: Apply to door count
Note on J34: Door hardware is damaged or non-functional and requires replacement
Note on L34: Door panel and hardware are damaged and require replacement
Note on N34: Door frame, door, and hardware are damaged and require replacement
Note on D35: Apply to door count
Note on J35: Door hardware is damaged or non-functional and requires replacement
Note on L35: Door panel and hardware are damaged and require replacement
Note on N35: Door frame, door, and hardware are damaged and require replacement
Note on D36: Apply to door count
Note on J36: Door hardware is damaged or non-functional and requires replacement
Note on L36: Door panel and hardware are damaged and require replacement
Note on N36: Door frame, door, and hardware are damaged and require replacement
Note on C38: Assumes the insulation, roof covering, and associated flashings, gutters, and downspouts
Note on D38: Apply to roof area
Note on H38: Small number of shingles lifting and/or separation in a portion of flashing
Note on J38: Leaks in a specific area or zone related to poor detailing and or flashing
Note on L38: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING
Note on N38: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on D39: Apply to roof area
Note on H39: Minor blistering requiring isolated patches
Note on J39: Leaks in a specific area or zone related to poor detailing and or flashing or unchecked blisters
Note on L39: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING
Note on N39: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on D40: Apply to roof area
Note on H40: Minor blistering requiring isolated patches
Note on J40: Leaks in a specific area or zone related to poor detailing and or flashing or seam separation
Note on L40: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Prep and re-coat roof system OVER TOP OF EXISTING
Note on N40: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on D41: Apply to roof area
Note on J41: Leaks are occurring and flashing at seams or transitions has separated requiring replacement of flashing and sealant
Note on N41: Panels have lifted or separated and water intrusion is evident. Remove and replace panels and associated flashing
Note on D42: Apply to roof area
Note on J42: Leaks occurring at isolated areas requiring grout removal and re-grout at isolated tile locations
Note on N42: Tiles are cracked, loose, or damaged and require removal and replacement
Note on D43: Apply to roof opening area
Note on J43: Minor leaking is occurring, requiring re-caulk and re-seal
Note on N43: The panes or framing are damaged beyond repair and requires replacement
Note on D44: Apply to roof opening area
Note on N44: The door is non-functional or damaged beyond repair and requires replacement
Note on D47: Apply to wall surface area
Note on N47: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on D48: Apply to wall surface area
Note on L48: There are some blocks that are damaged and requires a strategic removal and replacement
Note on N48: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on D49: Apply to door count
Note on J49: Door hardware is damaged or non-functional and requires replacement
Note on L49: Door panel and hardware are damaged and require replacement
Note on N49: Door frame, door, and hardware are damaged and require replacement
Note on D50: Apply to door count
Note on J50: Door hardware is damaged or non-functional and requires replacement
Note on L50: Door panel and hardware are damaged and require replacement
Note on N50: Door frame, door, and hardware are damaged and require replacement
Note on D53: Apply to stair flights
Note on L53: Rails not compliant with code and require removal and replacement
Note on N53: Structural integrity of stair unit is compromised and requires its removal and replacement
Note on D54: Apply to stair flights
Note on H54: Rust visible - prep and re-finish
Note on L54: Rails not compliant with code and require removal and replacement
Note on N54: Structural integrity of stair unit is compromised and requires its removal and replacement
Note on D55: Apply to stair flights
Note on L55: An isolated structural crack or separation requiring re-enforcement in place
Note on N55: Structural cracking and separation occurring in multiple locations - remove and replace the stair unit
Note on D56: Apply stair tread and riser area
Note on H56: Surface feels rough and/or taking in moisture from the surface resulting in staining - prep and re-seal
Note on N56: Severe cracking requiring removal and replacement of tread in fills
Note on D57: Apply stair tread and riser area
Note on N57: finish is lifting or separating and creating trip hazards - remove and replace
Note on D59: Apply to surface treated
Note on H59: Surface is in tact but finish is deteriorated - paint
Note on N59: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on D60: Apply to surface treated
Note on H60: Surface is in tact but finish is deteriorated - paint
Note on J60: Surface is damaged - patching of the surface is required prior to painting
Note on N60: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on D61: Apply to surface treated
Note on H61: Surface is in tact but finish is deteriorated - paint
Note on N61: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on D62: Apply to surface treated
Note on H62: Grout is damaged or deteriorated
Note on N62: Tiles are cracked or in disrepair
Note on D63: Apply to surface treated
Note on N63: worn or severely stained or starting to pull up / bubble
Note on D64: Apply to surface treated
Note on H64: sporadic number of tiles are lifting or cracked / broken and require replacement
Note on L64: The majority of tiles are lifting, cracking / broken and require replacement - the tiles or glue are NOT asbestos
Note on N64: The majority of tiles are lifting, cracking / broken and require replacement - the tiles or glue are asbestos
Note on D65: Apply to surface treated
Note on N65: Severely worn or seams separating - replace
Note on D66: Apply to surface treated
Note on H66: Surface feels rough and/or taking in moisture from the surface resulting in staining - prep and re-seal
Note on N66: Significant cracking, but not differential - requires prep and crack filling prior to re-seal. If differential, refer to slab on grade of floor construction above
Note on D67: Apply to surface treated
Note on H67: Grout is damaged or deteriorated
Note on N67: Tiles are cracked or in disrepair
Note on D68: Apply to surface treated
Note on N68: Systemic blistering or severely worn traffic areas - strip and replace
Note on D69: Apply to surface treated
Note on J69: Surface is damaged - requires sanding, repair, and re-coat / re-stripe
Note on N69: Wood planks are deteriorated, separating, and multiple dead spots - replace floor
Note on D70: Apply to surface treated
Note on H70: Surface is in tact but finish is deteriorated - paint
Note on J70: Surface is damaged - patching of the surface is required prior to painting
Note on N70: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on D71: Apply to surface treated
Note on H71: Stained or damaged ceiling tiles
Note on J71: Diagonal bracing missing from grid
Note on N71: Grid is sagging with tiles compromised - requires replacement of system
Note on D72: Apply to surface treated
Note on H72: Stained or damaged ceiling tiles
Note on N72: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on D73: Apply to surface treated
Note on N73: Surface is in tact but finish is deteriorated - paint
Note on C76: Assume standard cab-style elevator; Apply per stop
Note on E76: Insert number of elevators * number of stories - i.e. if there are 2 elevators each going 3 stories - insert 6
Note on H76: The elevator doors are damaged and require replacement
Note on J76: Electrical components are not working
Note on L76: Replacement of the hoist cables, guide rails, or other similar mechanical components is required
Note on N76: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C77: Apply per flight
Note on E77: Insert number of escalators * number of stories - i.e. if there are 2 escalators each going 3 stories - insert 6
Note on J77: Electrical components are not working
Note on N77: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C78: Assume open vertical or inclined lift; Apply per unit
Note on E78: Insert number of lifts
Note on J78: Electrical components are not working
Note on N78: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C80: All fixtures (toilets, urinals, sinks, showers, etc.) to be lumped together here
Note on J80: Flush valves or faucets are non-functional and require replacement
Note on N80: The fixture itself is broken or is not compliant with water efficiency standards
Note on H81: The vale stems, pressure gauges, and gate valves no longer function.
Note on J81: The insulation on the piping is in disrepair, loose, or missing.
Note on N81: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on H82: In some areas, there are back ups requiring the replacement of the broken floor or wall, clean outs, routing and cleaning the problem areas, and snaking floor drains
Note on N82: The runs and risers are deteriorated, displaced, or have systemic leaks and requires full replacement
Note on C83: This is for the presence of interior rain drains; note building percentage based on area of roof served - excludes external downspouts
Note on J83: The rain drain or overflow is damaged and needs replacement
Note on N83: The integrity of the piping is compromised and is leaking inside the walls
Note on C86: This assumes gas piping
Note on H86: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Note on N86: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on H87: The burner is inefficient and requires refurbishment
Note on J87: One major component needs to be replaced
Note on L87: More than one major component needs to be replaced
Note on N87: The system is in failure
Note on L88: Some of the distribution fans and coils are dysfunctional.
Note on N88: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Note on J89: A small number of minor parts need to be repaired or replaced
Note on L89: The burner, combustion chamber, or fan are faulty and require replacement
Note on N89: The entire furnace requires replacement
Note on J90: A small number of minor parts need to be repaired or replaced
Note on L90: System operating at low efficiency; shell exhibits corrosion. Retube heat exchanger
Note on N90: System operates at low efficiency with corrosion and leaks apparent. Replace system
Note on L91: Some of the distribution fans and coils are dysfunctional.
Note on N91: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Note on N92: The chiller is beyond economic repair
Note on J93: Dampers in the system are inoperative
Note on L93: The insulation is damaged or missing
Note on N93: The ductwork is damaged or inadequately designed and requires replacement
Note on H94: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Note on J94: The insulation on the piping is in disrepair, loose, or missing.
Note on N94: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on N95: Entire unit is failing to function
Note on J96: Internal compressor is bad and requires replacement
Note on N96: Entire unit is failing to function
Note on H97: In-room valve is failing and requires replacement
Note on N97: Entire unit is failing to function
Note on L98: Some of the sensors or valve actuators are dysfunctional. Replace these sensors or actuators
Note on N98: The majority of sensors or actuators are faulty, and the system software is dysfunctional OR the system is an older / obsolete pneumatic system - replace
Note on N99: One or more zones require re-balancing
Note on J102: Sprinkler heads are inoperable or non-compliant and need to be replaced
Note on N102: The piping has deteriorated or clogged or is non-compliant and needs to be replaced, including heads
Note on J103: The Siamese twin connection, tamper flow switches, or flow control valves are inoperable and need to be replaced
Note on N103: The fire pump is beyond repair and needs to be replaced
Note on C104: Assume chemical extinguishing system
Note on J104: The back-up tank has been discharged or lacks pressure and needs to be replaced
Note on N104: The system is non-functional or not compliant with the current needs and needs to be replaced
Note on J107: Wiring has systemic problems or does not meet code and needs to be replaced
Note on L107: Branch panels are obsolete with replacement breakers difficult to acquire and requires replacement
Note on N107: Main switchgear is obsolete or undersized and requires replacement, including service into building
Note on L108: The lighting fixtures are obsolete or non-functional and require replacement
Note on N108: Replacement of fixtures is requiring the replacement of the wiring as well - includes fixtures AND wiring
Note on J109: There are individual devices that are not functional.
Note on L109: The master control panel is obsolete or not functional
Note on N109: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on J110: There are individual devices that are not functional.
Note on L110: The master control panel is obsolete or not functional
Note on N110: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on J111: There are individual devices that are not functional.
Note on L111: The master control panel is obsolete or not functional
Note on N111: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on J112: There are individual devices that are not functional.
Note on L112: The master control panel is obsolete or not functional
Note on N112: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on J113: There are individual devices that are not functional.
Note on L113: The master control panel is obsolete or not functional
Note on N113: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on J114: There are individual devices that are not functional or in regular alarm
Note on L114: The master control panel is obsolete or not functional
Note on N114: The entire system is dysfunctional and constantly in trouble mode with areas not fully covered. Remove and replace system
Note on H115: Individual room sensors are failing and require replacement
Note on L115: The central control panel and software need upgraded
Note on N115: The entire system is in failure and requires replacement of sensors, wiring and central panel
Note on H120: 2-3 pieces of equipment require replacement
Note on J120: Counters and sinks are not code compliant and require replacement with stainless steel and sink system
Note on L120: Walk-in cooler and freezer are not functional or function intermittently and require replacement
Note on N120: Walk-ins and kitchen design does not meet current functional requirements or has become obsolete and requires complete replacement as a full prep kitchen
Note on H121: 2-3 pieces of equipment require replacement
Note on L121: Mechanical and electrical service upgrades are required to meet code and amount of program equipment
Note on N121: Both mechanical and electrical AND equipment needs replacement to meet program criteria and code
Note on J122: Room lacking (and needing) eye wash or fume hood
Note on L122: Sinks are in disrepair and require replacement
Note on N122: Work stations need upgrades to meet current program criteria - replace
Note on J123: Storage units damaged or in disrepair
Note on L123: Sinks are in disrepair and require replacement
Note on N123: Work stations need upgrades to meet current program criteria - replace
Note on E124: Insert number of seats
Note on J124: Seats damaged and need replacement OR sound OR lighting system inadequate and needs upgraded
Note on L124: Fly rigging in disrepair and needs upgrading
Note on N124: 2 or more stage system dysfunctional and needs upgrade / replacement to production systems
Note on H125: An accessory is damaged or missing
Note on J125: Accessories need to be replaced to meet ADA
Note on L125: The stall doors are not functional or missing and need to be replaced
Note on N125: The restrooms stall structure is failing or needs re-configuration and needs to be replaced
Note on D126: Note anything specific in the "Other" category at the bottom of the assessment form
Note on C129: Assume fixed casework (counters, cabinets, shelving, etc.)
Note on H129: The counter top or exposed surface has been damaged and can be refinished
Note on J129: The drawers and/or doors are damaged and require replacement including hardware
Note on L129: A combination of minor and moderate action is required, but the box is still salvageable
Note on N129: The casework is severely damaged throughout or is obsolete for the purposes of the space and needs to be replaced
Note on C130: Assume loose furnishings (desks, chairs, tables, etc.)
Note on N130: The furnishings are severely worn or are inappropriate for the age of students or function of space and require replacement
Note on C136: Paved only or needs to be paved; Apply to surface area
Note on E136: Indicate SF of road
Note on H136: Minor cracking exists and can be resolved with application of a slurry coat
Note on L136: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated
Note on N136: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel road and a paved one is needed, this category shall be used
Note on C137: Paved only or needs to be paved; Apply to surface area
Note on E137: Indicate number of stalls
Note on H137: Minor cracking exists and can be resolved with application of a slurry coat
Note on L137: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated
Note on N137: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel lot and a paved one is needed, this category shall be used
Note on C138: Concrete only or needs to be concrete; Apply to surface area
Note on E138: Indicate square footage of walks and plazas
Note on L138: Sections are broken with differential settlement requiring the removal of the effected panels and replacement
Note on N138: Not only are sections of the concrete broken, but there is evidence of settlement surrounding the walk requiring removal through sub-grade and replacement. Where there is no concrete walk, but one is needed, this category shall be used
Note on C139: Chain-link fencing; Apply to LF of fence
Note on E139: Indicate length of fencing - assuming 6' high chain-link
Note on L139: The fence fabric is damaged and needs to be replaced
Note on N139: The fencing has lost its structural integrity and is beyond repair.
Note on C140: Irrigation systems. Other landscape or field items should be included in "Other" category at bottom of assessment form; Apply to landscape area
Note on E140: Indicate square footage of landscaped area served (including grass areas)
Note on N140: Irrigation system is dysfunctional and beyond repair
Note on D142: Assumes 4" line to building. Wells should be placed in "Other" category at bottom of form; Apply to surface area
Note on N142: A portion of the line has lost its structural integrity and requires replacement
Note on D143: Assumes 6" line to building. Wells and holding tanks should be placed in "Other" category at bottom of form; Apply to surface area
Note on N143: A portion of the line has lost its structural integrity and requires replacement
Note on C144: Lines only. Septic fields, tanks, etc. should be placed in "other" category at bottom of form; Apply to surface area
Note on N144: A portion of the line has lost its structural integrity and requires replacement
Note on C145: Assumes underground system. For surface runoff system, apply to "Other" category at bottom of form; Apply to surface area
Note on H145: Catch basins have lost their integrity or are out of alignment. Remove catch basin, reset, and realign
Note on J145: Storm sewer piping is dysfunctional or damaged. Remove and replace.
Note on L145: Detention/retention has failed, but piping and catch basins are functional. Replace detention / retention system
Note on N145: The entire underground system has failed and requires removal and replacement of all components
Note on C146: Apply to surface area
Note on N146: A portion of the line has lost its structural integrity and requires replacement
Note on C147: Apply to surface area
Note on N147: A portion of the line has lost its structural integrity and requires replacement
Note on C148: Natural gas lines; Apply to surface area
Note on N148: A portion of the line has lost its structural integrity and requires replacement
Note on D151: Assumes the private portion of the service lines typically underground after the meter or transformer; Apply to surface area
Note on L151: The transformer no longer functions and is in need of replacement
Note on N151: The service has failed and is beyond repair or is undersized requiring replacement of transformer and service lines
Note on D152: Apply to generator quantity
Note on H152: The generator needs to be tuned up
Note on J152: The valves or other engine parts need to be repaired or replaced and then a tune up
Note on L152: Generator is non-functional or under-sized
Note on N152: The system (generator, tank, services lines connected lighting system) is non-functional or under-sized
Note on C153: Apply to surface area
Note on J153: The fixtures are nonfunctional and require replacement
Note on N153: The fixtures, supports, and underground wiring need to be replaced
Note on C154: Assumes low voltage lines underground; Apply to surface area
Note on N154: Site cabling is inadequate or service is interrupted - replace cabling
Note on C158: For assessment professional to hand enter for specialty items and systems that do not fit into categories above

## PCA Cost Tables - READ ONLY
District Name: |  | Lincoln County SD |  |  | State Assigned Inflation Factor | 1.1 | Inflation Assigned for a 30-month period assuming 1 year till bond and 1-1/2 years into a 3-year design/construction cycle
Site Name: |  | Taft Elementary School |  |  | State Assigned Soft Development Factor | 1.38 | Assuming design, direct-hire specialists (envelope, commissioning, cost estimating, etc.), state solar, permits, survey, geo, bond issuance, management, furnishings, and 15% contingency
Building Name: |  | Main
Building ID: |  | N/A
LEVEL OF ACTION
Level 1 | Level 2 | Level 3 | Type (as applicable) |  | Minor |  | Moderate |  | Major |  | Replace | Forwarded Unit Budget | Cost Estimator Notes
A SUBSTRUCTURE
A10 Foundations
|  | A1010 Standard Foundations |  | 1 | Minor |  | Moderate | 20 | Major |  | Replace | 0 | Apply rates to bldg footprint area
|  | A1020 Special Foundations |  | 1 | Minor |  | Moderate | 35 | Major |  | Replace | 0 | Apply rates to bldg footprint area
|  | A1030 Slab on Grade |  |  | Minor | 5 | Moderate | 12 | Major |  | Replace | 0 | Apply rates to bldg footprint area
A20 Basement Construction
|  | A2010 Basement Excavation | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace | 0
|  | A2020 Basement Walls |  | 10 | Minor | 15 | Moderate | 20 | Major |  | Replace | 0 | Apply to wall surface area
B SHELL
B10 Superstructure
|  | B1010 Floor Construction | Wood |  | Minor | 10 | Moderate |  | Major | 25 | Replace | 0
|  |  | Steel |  | Minor | 15 | Moderate |  | Major | 35 | Replace | 0
|  |  | Concrete |  | Minor | 25 | Moderate |  | Major | 45 | Replace | 0
|  | B1020 Roof Construction | Wood |  | Minor |  | Moderate | 15 | Major | 20 | Replace | 0
|  |  | Steel |  | Minor |  | Moderate | 20 | Major | 25 | Replace | 0
|  |  | Concrete |  | Minor |  | Moderate | 25 | Major | 32 | Replace | 0
B20 Exterior Enclosure
|  | B2010 Exterior Walls | Concrete Formed / Tilt |  | Minor | 4 | Moderate | 7 | Major |  | Replace | 0 | Apply to wall surface area
|  |  | Masonry |  | Minor | 6 | Moderate | 10 | Major | 32 | Replace | 0 | Apply to wall surface area
|  |  | Framed w/Panel Siding |  | Minor | 6 | Moderate | 10 | Major | 30 | Replace | 6 | Apply to wall surface area
|  |  | Framed w/Stucco |  | Minor | 4 | Moderate | 8 | Major | 25 | Replace | 0 | Apply to wall surface area
|  |  | Framed w/Masonry Veneer |  | Minor | 5 | Moderate | 10 | Major | 35 | Replace | 0 | Apply to wall surface area
|  | B2020 Exterior Windows | Wood |  | Minor | 9 | Moderate | 12 | Major | 20 | Replace | 0 | Apply to glazed area
|  |  | Aluminum |  | Minor | 5 | Moderate | 8 | Major | 13 | Replace | 0 | Apply to glazed area
|  |  | Clad |  | Minor | 4 | Moderate | 7 | Major | 10 | Replace | 4 | Apply to glazed area
|  |  | Curtain Wall |  | Minor | 1.5 | Moderate | 2.7 | Major | 25 | Replace | 0 | Apply to glazed area
|  | B2030 Exterior Doors | Wood |  | Minor | 300 | Moderate | 1000 | Major | 1500 | Replace | 0 | Apply to door count
|  |  | Hollow Metal |  | Minor | 300 | Moderate | 850 | Major | 1300 | Replace | 300 | Apply to door count
|  |  | Storefront |  | Minor | 500 | Moderate | 1400 | Major | 2100 | Replace | 0 | Apply to door count
B30 Roofing
|  | B3010 Roof Coverings | Asphalt Shingle | 1.2 | Minor | 2.5 | Moderate | 4 | Major | 7 | Replace | 0 | Apply to roof area
|  |  | Built-Up | 1.4 | Minor | 4 | Moderate | 7 | Major | 10 | Replace | 10 | Apply to roof area
|  |  | Single Ply | 2.1 | Minor | 6 | Moderate | 10 | Major | 14 | Replace | 0 | Apply to roof area
|  |  | Metal |  | Minor | 9 | Moderate |  | Major | 20 | Replace | 0 | Apply to roof area
|  |  | Concrete Tile |  | Minor | 9 | Moderate |  | Major | 25 | Replace | 0 | Apply to roof area
|  | B3020 Roof Openings | Skylights |  | Minor | 25 | Moderate |  | Major | 75 | Replace | 0 | Apply to roof opening area
|  |  | Access Hatch |  | Minor |  | Moderate |  | Major | 20 | Replace | 0 | Apply to roof opening area
C INTERIORS
C10 Interior Construction
|  | C1010 Partitions | Framed |  | Minor |  | Moderate |  | Major | 20 | Replace | 0 | Apply to wall surface area
|  |  | Masonry |  | Minor |  | Moderate | 20 | Major | 29 | Replace | 0 | Apply to wall surface area
|  | C1020 Interior Doors | Wood |  | Minor | 300 | Moderate | 900 | Major | 1300 | Replace | 1300 | Apply to door count
|  |  | Hollow Metal |  | Minor | 300 | Moderate | 750 | Major | 1100 | Replace | 1100 | Apply to door count
|  | C1030 Fittings | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace | 0
C20 Stairs
|  | C2010 Stair Construction | Wood |  | Minor |  | Moderate | 20000 | Major | 50000 | Replace | 0 | Apply to stair flights
|  |  | Metal | 5000 | Minor |  | Moderate | 17000 | Major | 40000 | Replace | 0 | Apply to stair flights
|  |  | Concrete |  | Minor |  | Moderate | 10000 | Major | 35000 | Replace | 0 | Apply to stair flights
|  | C2020 Stair Finishes | Concrete Fill | 5000 | Minor |  | Moderate |  | Major | 5 | Replace | 0 | Apply stair tread and riser area
|  |  | Resilient |  | Minor |  | Moderate |  | Major | 10 | Replace | 0 | Apply stair tread and riser area
C30 Interior Finishes
|  | C3010 Wall Finishes | Paint on Masonry | 1.5 | Minor |  | Moderate |  | Major | 2 | Replace | 0 | Apply to surface treated
|  |  | Wallboard | 1.5 | Minor | 3 | Moderate |  | Major | 6 | Replace | 0 | Apply to surface treated
|  |  | Wainscot | 1.5 | Minor |  | Moderate |  | Major | 12 | Replace | 12 | Apply to surface treated
|  |  | Ceramic Tile | 1 | Minor |  | Moderate |  | Major | 20 | Replace | 0 | Apply to surface treated
|  | C3020 Floor Finishes | Carpet / Soft Surface |  | Minor |  | Moderate |  | Major | 5.85 | Replace | 0 | Apply to surface treated
|  |  | Resilient Tile | 2.5 | Minor |  | Moderate | 5 | Major | 5.5 | Replace | 5.5 | Apply to surface treated
|  |  | Resilient Sheet |  | Minor |  | Moderate |  | Major | 6 | Replace | 0 | Apply to surface treated
|  |  | Polished Concrete | 2.5 | Minor |  | Moderate |  | Major | 7.5 | Replace | 0 | Apply to surface treated
|  |  | Ceramic Tile | 5 | Minor |  | Moderate |  | Major | 18 | Replace | 0 | Apply to surface treated
|  |  | Liquid Applied |  | Minor |  | Moderate |  | Major | 16 | Replace | 0 | Apply to surface treated
|  |  | Wood Sports Floor |  | Minor | 6.25 | Moderate |  | Major | 28.5 | Replace | 0 | Apply to surface treated
|  | C3030 Ceiling Finishes | Wallboard | 1.5 | Minor | 2.5 | Moderate |  | Major | 8.5 | Replace | 0 | Apply to surface treated
|  |  | Lay-In Ceiling Tile | 1.5 | Minor | 2.5 | Moderate |  | Major | 5.1 | Replace | 0 | Apply to surface treated
|  |  | Glued-Up Ceiling Tile | 1.85 | Minor |  | Moderate |  | Major | 4.5 | Replace | 4.5 | Apply to surface treated
|  |  | Painted Structure |  | Minor |  | Moderate |  | Major | 2.5 | Replace | 0 | Apply to surface treated
D SERVICES
D10 Conveying
|  | D1010 Elevators & Lifts |  | 6000 | Minor | 10000 | Moderate | 20000 | Major | 40000 | Replace | 0 | Apply per stop
|  | D1020 Escalators & Moving Walks |  |  | Minor | 20000 | Moderate |  | Major | 150000 | Replace | 0 | Apply per flight
|  | D1090 Other Conveying Systems |  |  | Minor | 5000 | Moderate |  | Major | 25000 | Replace | 0 | Apply per unit
D20 Plumbing
|  | D2010 Plumbing Fixtures |  |  | Minor | 4 | Moderate |  | Major | 7 | Replace | 11
|  | D2020 Domestic Water Distribution |  | 2.5 | Minor | 2 | Moderate |  | Major | 3 | Replace | 3
|  | D2030 Sanitary Waste |  | 2.5 | Minor |  | Moderate |  | Major | 3 | Replace | 0
|  | D2040 Rain Water Drainage |  |  | Minor | 1 | Moderate |  | Major | 1.5 | Replace | 0
|  | D2090 Other Plumbing Systems | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace | 0
D30 HVAC
|  | D3010 Energy Supply |  | 2 | Minor |  | Moderate |  | Major | 1 | Replace | 0
|  | D3020 Heat Generating Systems | Boiler | 1.5 | Minor | 2.5 | Moderate | 3 | Major | 4 | Replace | 0
|  |  | Air Handler |  | Minor |  | Moderate | 2 | Major | 3 | Replace | 3
|  |  | Furnace |  | Minor | 2.5 | Moderate | 1.5 | Major | 2 | Replace | 0
|  |  | Heat Exchanger |  | Minor | 2.5 | Moderate | 2 | Major | 2.5 | Replace | 0
|  | D3030 Cooling Generating Systems | Component of air handler |  | Minor |  | Moderate | 2 | Major | 3 | Replace | 0
|  |  | Stand alone chiller |  | Minor |  | Moderate |  | Major | 5 | Replace | 0
|  | D3040 Distribution Systems | Ductwork |  | Minor | 3 | Moderate | 1 | Major | 2 | Replace | 0
|  |  | Hot water return & supply | 1.5 | Minor | 3 | Moderate |  | Major | 5 | Replace | 3
|  | D3050 Terminal & Package Units | Above ceiling VAV unit |  | Minor |  | Moderate |  | Major | 2 | Replace | 0
|  |  | In-room ventilator unit |  | Minor | 3 | Moderate |  | Major | 2 | Replace | 0
|  |  | In-room radiant unit | 1 | Minor |  | Moderate |  | Major | 1 | Replace | 0
|  | D3060 Controls & Instrumentation |  |  | Minor |  | Moderate | 1 | Major | 2 | Replace | 0
|  | D3070 Systems Testing & Balancing |  |  | Minor |  | Moderate |  | Major | 1 | Replace | 0
|  | D3090 Other HVAC Systems & Equipment | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace | 0
D40 Fire Protection
|  | D4010 Sprinklers |  |  | Minor | 2 | Moderate |  | Major | 3.75 | Replace | 2
|  | D4020 Standpipes |  |  | Minor | 1.5 | Moderate |  | Major | 2 | Replace | 0
|  | D4030 Fire Protection Specialties |  |  | Minor | 1.5 | Moderate |  | Major | 2 | Replace | 0
|  | D4090 Other Fire Protection Systems | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace | 0
D50 Electrical
|  | D5010 Electrical Service & Distribution |  |  | Minor | 3 | Moderate | 5.6 | Major | 8 | Replace | 0
|  | D5020 Lighting and Branch Wiring |  |  | Minor |  | Moderate | 6 | Major | 12 | Replace | 0
|  | D5030 Communications & Security | Voice / Data System |  | Minor | 1.5 | Moderate | 3 | Major | 5.5 | Replace | 5.5
|  |  | Clock / Intercom System |  | Minor | 1.5 | Moderate | 2.5 | Major | 5 | Replace | 2.5
|  |  | Closed Circuit Surveillance |  | Minor | 0.25 | Moderate | 0.65 | Major | 1.1 | Replace | 0.65
|  |  | Access Control System |  | Minor | 0.25 | Moderate | 0.5 | Major | 1 | Replace | 0
|  |  | Intrusion Alarm System |  | Minor | 0.15 | Moderate | 0.25 | Major | 0.65 | Replace | 0
|  |  | Fire Alarm / Detection |  | Minor | 0.5 | Moderate | 1 | Major | 2.25 | Replace | 2.25
|  |  | Lighting Control System | 0.25 | Minor |  | Moderate | 0.5 | Major | 1 | Replace | 0
|  | D5090 Other Electrical Systems | NOT USED |  | Minor |  | Moderate |  | Major | 5.5 | Replace | 0
E EQUIPMENT & FURNISHINGS
E10 Equipment
|  | E1010 Commercial Equipment | Food Service | 0.4 | Minor | 0.65 | Moderate | 0.8 | Major | 2 | Replace | 0.65
|  |  | Vocational | 0.4 | Minor |  | Moderate | 0.65 | Major | 1.65 | Replace | 0
|  | E1020 Institutional Equipment | Science |  | Minor | 20000 | Moderate | 1.5 | Major | 3.5 | Replace | 0
|  |  | Art |  | Minor | 2500 | Moderate | 1.5 | Major | 3 | Replace | 0
|  |  | Stage Performance |  | Minor | 560 | Moderate | 20000 | Major | 75000 | Replace | 0
|  |  | Restroom Accessories/Stalls | 5 | Minor | 7.5 | Moderate | 12 | Major | 25 | Replace | 25
|  | E1030 Vehicular Equipment | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace | 0
|  | E1090 Other Equipment | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace | 0
E20 Furnishings
|  | E2010 Fixed Furnishings |  | 1.5 | Minor | 3 | Moderate | 6 | Major | 12 | Replace | 6
|  | E2020 Movable Furnishings |  |  | Minor |  | Moderate |  | Major | 18 | Replace | 0
F SPECIAL CONSTRUCTION & DEMOLITION - NOT USED
G BUILDING SITE WORK
| G10 Site Preparation |  | NOT USED
G20 Site Improvements
|  | G2010 Roadways |  | 1.4 | Minor |  | Moderate | 11 | Major | 9.5 | Replace | 0 | Apply to surface area
|  | G2020 Parking Lots |  | 3 | Minor |  | Moderate | 9 | Major | 6.5 | Replace | 3 | Apply to surface area
|  | G2030 Pedestrian Paving |  |  | Minor |  | Moderate | 12 | Major | 10 | Replace | 0 | Apply to surface area
|  | G2040 Site Development |  |  | Minor |  | Moderate | 1 | Major | 65 | Replace | 0 | Apply to LF of fence
|  | G2050 Landscaping |  |  | Minor |  | Moderate |  | Major | 2.85 | Replace | 0 | Apply to landscape area
G30 Site Mechanical Utilities
|  | G3010 Water Supply | Domestic |  | Minor |  | Moderate |  | Major | 1 | Replace | 0 | Apply to surface area
|  |  | Fire |  | Minor |  | Moderate |  | Major | 2.5 | Replace | 0 | Apply to surface area
|  | G3020 Sanitary Sewer |  |  | Minor |  | Moderate |  | Major | 1 | Replace | 0 | Apply to surface area
|  | G3030 Storm Sewer |  | 0.65 | Minor | 1 | Moderate | 1.5 | Major | 2.5 | Replace | 0 | Apply to surface area
|  | G3040 Heating Distribution |  |  | Minor |  | Moderate |  | Major | 3 | Replace | 0 | Apply to surface area
|  | G3050 Cooling Distribution |  |  | Minor |  | Moderate |  | Major | 3 | Replace | 0 | Apply to surface area
|  | G3060 Fuel Distribution |  |  | Minor |  | Moderate |  | Major | 1 | Replace | 0 | Apply to surface area
|  | G3090 Other Site Mechanical Utilities | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace | 0
G40 Site Electrical Utilities
|  | G4010 Electrical Distribution | Service |  | Minor |  | Moderate | 1.5 | Major | 3 | Replace | 0 | Apply to surface area
|  |  | Generator | 2500 | Minor | 15000 | Moderate | 90000 | Major | 90000 | Replace | 0 | Apply to generator quantity
|  | G4020 Site Lighting |  |  | Minor | 15000 | Moderate |  | Major | 3 | Replace | 0 | Apply to surface area
|  | G4030 Site Communications & Security |  |  | Minor |  | Moderate |  | Major | 2 | Replace | 0 | Apply to surface area
|  | G4090 Other Site Electrical Utilities | NOT USED |  | Minor |  | Moderate |  | Major |  | Replace | 0
| G90 Other Site Construction |  | NOT USED
Note on C10: Standard spread and strip / perimeter footings
Note on E10: Minor cracking observed - fill and seal the cracks to prevent water intrusion
Note on I10: Settlement observed in surrounding conditions - requiring stabilization of the foundation, sub-grade adjustment, and re-enforcement of the foundation
Note on C11: Pilings or other extended foundation systems that overcome non-standard soil conditions
Note on E11: Minor cracking observed - fill and seal the cracks to prevent water intrusion
Note on I11: Settlement observed in surrounding conditions - requiring stabilization of the foundation, sub-grade adjustment, and re-enforcement of the foundation
Note on C12: Standard ground-set concrete slab. If slab is elevated (i.e. has a crawl space or basement), apply conditions to B1010 instead
Note on G12: Separation cracks occurring requiring route and fill and patch
Note on I12: Differential settlement occurring - requires removal of section of slab, adjustment to sub-grade, and new infill
Note on C15: Assumed as concrete walls with water-proofing on the exterior. Includes only the structural portion and not the wall finishes
Note on E15: Inadequate below grade venting is observed - cut in and add venting
Note on G15: Wall is cracked and spalling requiring route and fill and patch and re-finish
Note on I15: Wall is cracked with evidence of water intrusion. Repairs to be implemented and water barrier to be applied to be applied
Note on C18: A suspended floor including the structural members and floor construction, but not including the actual finish
Note on G18: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck
Note on K18: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on G19: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck
Note on K19: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on G20: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck
Note on K20: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on C21: The roof structure referring to the supporting structure and the deck but excluding the roofing itself
Note on I21: Evidence of a spongy decking from water intrusion - replacing the deck but not the trusses
Note on K21: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on I22: Evidence of a flexing decking from water intrusion / rust - replacing the deck but not the trusses
Note on K22: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on I23: Evidence of a spongy / spalling deck from water intrusion - replacing the deck but not the beams
Note on K23: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on G25: Surface is in tact but finish is deteriorated - paint
Note on I25: Cracks visible - route and patch prior to painting
Note on G26: Surface is in tact but finish is deteriorated - paint
Note on I26: Some blocks are damaged, needing patch and repair prior to sealing or painting
Note on K26: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on G27: Surface is in tact but finish is deteriorated - paint
Note on I27: A number of panels are damaged, requiring patch and repair prior to re-painting
Note on K27: The panels are lifting or separating or otherwise losing their integrity - remove and replace
Note on G28: Surface is in tact but finish is deteriorated - paint
Note on I28: Cracks visible - route and patch prior to painting
Note on K28: System in failure with evidence of water intrusion - remove and replace
Note on G29: Minor repairs needed to mortar, prep, and re-sealing
Note on I29: Mortar missing in a majority of areas requiring complete re-pointing and sealing
Note on K29: Masonry visibly damaged and requiring removal and replacement
Note on G30: The glazing is double pane but is broken or fogged and requires replacement
Note on I30: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing
Note on K30: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D31: This assumes both individual aluminum windows and storefront systems
Note on G31: The glazing is double pane but is broken or fogged and requires replacement
Note on I31: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing
Note on K31: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D32: This assumes a metal windows system clad with wood or vinyl
Note on G32: The glazing is double pane but is broken or fogged and requires replacement
Note on I32: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing
Note on K32: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on G33: Minor leaks at wall seams - re-caulk and re-seal
Note on I33: Window panels fogged and require replacement
Note on K33: Settlement or displacement is evident
Note on G34: Door hardware is damaged or non-functional and requires replacement
Note on I34: Door panel and hardware are damaged and require replacement
Note on K34: Door frame, door, and hardware are damaged and require replacement
Note on G35: Door hardware is damaged or non-functional and requires replacement
Note on I35: Door panel and hardware are damaged and require replacement
Note on K35: Door frame, door, and hardware are damaged and require replacement
Note on G36: Door hardware is damaged or non-functional and requires replacement
Note on I36: Door panel and hardware are damaged and require replacement
Note on K36: Door frame, door, and hardware are damaged and require replacement
Note on C38: Assumes the insulation, roof covering, and associated flashings, gutters, and downspouts
Note on E38: Small number of shingles lifting and/or separation in a portion of flashing
Note on G38: Leaks in a specific area or zone related to poor detailing and or flashing
Note on I38: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING
Note on K38: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on E39: Minor blistering requiring isolated patches
Note on G39: Leaks in a specific area or zone related to poor detailing and or flashing or unchecked blisters
Note on I39: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING
Note on K39: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on E40: Minor blistering requiring isolated patches
Note on G40: Leaks in a specific area or zone related to poor detailing and or flashing or seam separation
Note on I40: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Prep and re-coat roof system OVER TOP OF EXISTING
Note on K40: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on G41: Leaks are occurring and flashing at seams or transitions has separated requiring replacement of flashing and sealant
Note on K41: Panels have lifted or separated and water intrusion is evident. Remove and replace panels and associated flashing
Note on G42: Leaks occurring at isolated areas requiring grout removal and re-grout at isolated tile locations
Note on K42: Tiles are cracked, loose, or damaged and require removal and replacement
Note on G43: Minor leaking is occurring, requiring re-caulk and re-seal
Note on K43: The panes or framing are damaged beyond repair and requires replacement
Note on K44: The door is non-functional or damaged beyond repair and requires replacement
Note on K47: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on I48: There are some blocks that are damaged and requires a strategic removal and replacement
Note on K48: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on G49: Door hardware is damaged or non-functional and requires replacement
Note on I49: Door panel and hardware are damaged and require replacement
Note on K49: Door frame, door, and hardware are damaged and require replacement
Note on G50: Door hardware is damaged or non-functional and requires replacement
Note on I50: Door panel and hardware are damaged and require replacement
Note on K50: Door frame, door, and hardware are damaged and require replacement
Note on I53: Rails not compliant with code and require removal and replacement
Note on K53: Structural integrity of stair unit is compromised and requires its removal and replacement
Note on E54: Rust visible - prep and re-finish
Note on I54: Rails not compliant with code and require removal and replacement
Note on K54: Structural integrity of stair unit is compromised and requires its removal and replacement
Note on I55: An isolated structural crack or separation requiring re-enforcement in place
Note on K55: Structural cracking and separation occurring in multiple locations - remove and replace the stair unit
Note on E56: Surface feels rough and/or taking in moisture from the surface resulting in staining - prep and re-seal
Note on K56: Severe cracking requiring removal and replacement of tread in fills
Note on K57: finish is lifting or separating and creating trip hazards - remove and replace
Note on E59: Surface is in tact but finish is deteriorated - paint
Note on K59: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on E60: Surface is in tact but finish is deteriorated - paint
Note on G60: Surface is damaged - patching of the surface is required prior to painting
Note on K60: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on E61: Surface is in tact but finish is deteriorated - paint
Note on K61: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on E62: Grout is damaged or deteriorated
Note on K62: Tiles are cracked or in disrepair
Note on K63: worn or severely stained or starting to pull up / bubble
Note on E64: sporadic number of tiles are lifting or cracked / broken and require replacement
Note on I64: The majority of tiles are lifting, cracking / broken and require replacement - the tiles or glue are NOT asbestos
Note on K64: The majority of tiles are lifting, cracking / broken and require replacement - the tiles or glue are asbestos
Note on K65: Severely worn or seams separating - replace
Note on E66: Surface feels rough and/or taking in moisture from the surface resulting in staining - prep and re-seal
Note on K66: Significant cracking, but not differential - requires prep and crack filling prior to re-seal. If differential, refer to slab on grade of floor construction above
Note on E67: Grout is damaged or deteriorated
Note on K67: Tiles are cracked or in disrepair
Note on K68: Systemic blistering or severely worn traffic areas - strip and replace
Note on G69: Surface is damaged - requires sanding, repair, and re-coat / re-stripe
Note on K69: Wood planks are deteriorated, separating, and multiple dead spots - replace floor
Note on E70: Surface is in tact but finish is deteriorated - paint
Note on G70: Surface is damaged - patching of the surface is required prior to painting
Note on K70: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on E71: Stained or damaged ceiling tiles
Note on G71: Diagonal bracing missing from grid
Note on K71: Grid is sagging with tiles compromised - requires replacement of system
Note on E72: Stained or damaged ceiling tiles
Note on K72: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on K73: Surface is in tact but finish is deteriorated - paint
Note on C76: Assume standard cab-style elevator
Note on E76: The elevator doors are damaged and require replacement
Note on G76: Electrical components are not working
Note on I76: Replacement of the hoist cables, guide rails, or other similar mechanical components is required
Note on K76: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on G77: Electrical components are not working
Note on K77: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C78: Assume open vertical or inclined lift
Note on G78: Electrical components are not working
Note on K78: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C80: All fixtures (toilets, urinals, sinks, showers, etc.) to be lumped together here
Note on G80: Flush valves or faucets are non-functional and require replacement
Note on K80: The fixture itself is broken or is not compliant with water efficiency standards
Note on E81: The vale stems, pressure gauges, and gate valves no longer function.
Note on G81: The insulation on the piping is in disrepair, loose, or missing.
Note on K81: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on E82: In some areas, there are back ups requiring the replacement of the broken floor or wall, clean outs, routing and cleaning the problem areas, and snaking floor drains
Note on K82: The runs and risers are deteriorated, displaced, or have systemic leaks and requires full replacement
Note on C83: This is for the presence of interior rain drains; note building percentage based on area of roof served - excludes external downspouts
Note on G83: The rain drain or overflow is damaged and needs replacement
Note on K83: The integrity of the piping is compromised and is leaking inside the walls
Note on C86: This assumes gas piping
Note on E86: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Note on K86: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on E87: The burner is inefficient and requires refurbishment
Note on G87: One major component needs to be replaced
Note on I87: More than one major component needs to be replaced
Note on K87: The system is in failure
Note on I88: Some of the distribution fans and coils are dysfunctional.
Note on K88: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Note on G89: A small number of minor parts need to be repaired or replaced
Note on I89: The burner, combustion chamber, or fan are faulty and require replacement
Note on K89: The entire furnace requires replacement
Note on G90: A small number of minor parts need to be repaired or replaced
Note on I90: System operating at low efficiency; shell exhibits corrosion. Retube heat exchanger
Note on K90: System operates at low efficiency with corrosion and leaks apparent. Replace system
Note on I91: Some of the distribution fans and coils are dysfunctional.
Note on K91: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Note on K92: The chiller is beyond economic repair
Note on G93: Dampers in the system are inoperative
Note on I93: The insulation is damaged or missing
Note on K93: The ductwork is damaged or inadequately designed and requires replacement
Note on E94: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Note on G94: The insulation on the piping is in disrepair, loose, or missing.
Note on K94: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on K95: Entire unit is failing to function
Note on G96: Internal compressor is bad and requires replacement
Note on K96: Entire unit is failing to function
Note on E97: In-room valve is failing and requires replacement
Note on K97: Entire unit is failing to function
Note on I98: Some of the sensors or valve actuators are dysfunctional. Replace these sensors or actuators
Note on K98: The majority of sensors or actuators are faulty, and the system software is dysfunctional OR the system is an older / obsolete pneumatic system - replace
Note on K99: One or more zones require re-balancing
Note on G102: Sprinkler heads are inoperable or non-compliant and need to be replaced
Note on K102: The piping has deteriorated or clogged or is non-compliant and needs to be replaced, including heads
Note on G103: The Siamese twin connection, tamper flow switches, or flow control valves are inoperable and need to be replaced
Note on K103: The fire pump is beyond repair and needs to be replaced
Note on C104: Assume chemical extinguishing system
Note on G104: The back-up tank has been discharged or lacks pressure and needs to be replaced
Note on K104: The system is non-functional or not compliant with the current needs and needs to be replaced
Note on G107: Wiring has systemic problems or does not meet code and needs to be replaced
Note on I107: Branch panels are obsolete with replacement breakers difficult to acquire and requires replacement
Note on K107: Main switchgear is obsolete or undersized and requires replacement, including service into building
Note on I108: The lighting fixtures are obsolete or non-functional and require replacement
Note on K108: Replacement of fixtures is requiring the replacement of the wiring as well - includes fixtures AND wiring
Note on G109: There are individual devices that are not functional.
Note on I109: The master control panel is obsolete or not functional
Note on K109: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on G110: There are individual devices that are not functional.
Note on I110: The master control panel is obsolete or not functional
Note on K110: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on G111: There are individual devices that are not functional.
Note on I111: The master control panel is obsolete or not functional
Note on K111: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on G112: There are individual devices that are not functional.
Note on I112: The master control panel is obsolete or not functional
Note on K112: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on G113: There are individual devices that are not functional.
Note on I113: The master control panel is obsolete or not functional
Note on K113: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on G114: There are individual devices that are not functional or in regular alarm
Note on I114: The master control panel is obsolete or not functional
Note on K114: The entire system is dysfunctional and constantly in trouble mode with areas not fully covered. Remove and replace system
Note on E115: Individual room sensors are failing and require replacement
Note on I115: The central control panel and software need upgraded
Note on K115: The entire system is in failure and requires replacement of sensors, wiring and central panel
Note on E120: 2-3 pieces of equipment require replacement
Note on G120: Counters and sinks are not code compliant and require replacement with stainless steel and sink system
Note on I120: Walk-in cooler and freezer are not functional or function intermittently and require replacement
Note on K120: Walk-ins and kitchen design does not meet current functional requirements or has become obsolete and requires complete replacement as a full prep kitchen
Note on E121: 2-3 pieces of equipment require replacement
Note on I121: Mechanical and electrical service upgrades are required to meet code and amount of program equipment
Note on K121: Both mechanical and electrical AND equipment needs replacement to meet program criteria and code
Note on G122: Room lacking (and needing) eye wash or fume hood
Note on I122: Sinks are in disrepair and require replacement
Note on K122: Work stations need upgrades to meet current program criteria - replace
Note on G123: Storage units damaged or in disrepair
Note on I123: Sinks are in disrepair and require replacement
Note on K123: Work stations need upgrades to meet current program criteria - replace
Note on G124: Seats damaged and need replacement OR sound OR lighting system inadequate and needs upgraded
Note on I124: Fly rigging in disrepair and needs upgrading
Note on K124: 2 or more stage system dysfunctional and needs upgrade / replacement to production systems
Note on E125: An accessory is damaged or missing
Note on G125: Accessories need to be replaced to meet ADA
Note on I125: The stall doors are not functional or missing and need to be replaced
Note on K125: The restrooms stall structure is failing or needs re-configuration and needs to be replaced
Note on D126: Note anything specific in the "Other" category at the bottom of the assessment form
Note on C129: Assume fixed casework (counters, cabinets, shelving, etc.)
Note on E129: The counter top or exposed surface has been damaged and can be refinished
Note on G129: The drawers and/or doors are damaged and require replacement including hardware
Note on I129: A combination of minor and moderate action is required, but the box is still salvageable
Note on K129: The casework is severely damaged throughout or is obsolete for the purposes of the space and needs to be replaced
Note on C130: Assume loose furnishings (desks, chairs, tables, etc.)
Note on K130: The furnishings are severely worn or are inappropriate for the age of students or function of space and require replacement
Note on C136: Paved only or needs to be paved
Note on E136: Minor cracking exists and can be resolved with application of a slurry coat
Note on I136: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated
Note on K136: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel road and a paved one is needed, this category shall be used
Note on C137: Paved only or needs to be paved
Note on E137: Minor cracking exists and can be resolved with application of a slurry coat
Note on I137: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated
Note on K137: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel lot and a paved one is needed, this category shall be used
Note on C138: Concrete only or needs to be concrete
Note on I138: Sections are broken with differential settlement requiring the removal of the effected panels and replacement
Note on K138: Not only are sections of the concrete broken, but there is evidence of settlement surrounding the walk requiring removal through sub-grade and replacement. Where there is no concrete walk, but one is needed, this category shall be used
Note on C139: Chain-link fencing
Note on I139: The fence fabric is damaged and needs to be replaced
Note on K139: The fencing has lost its structural integrity and is beyond repair.
Note on C140: Irrigation systems. Other landscape or field items should be included in "Other" category at bottom of assessment form
Note on K140: Irrigation system is dysfunctional and beyond repair
Note on D142: Assumes 4" line to building. Wells should be placed in "Other" category at bottom of form
Note on K142: A portion of the line has lost its structural integrity and requires replacement
Note on D143: Assumes 6" line to building. Wells and holding tanks should be placed in "Other" category at bottom of form
Note on K143: A portion of the line has lost its structural integrity and requires replacement
Note on C144: Lines only. Septic fields, tanks, etc. should be placed in "other" category at bottom of form
Note on K144: A portion of the line has lost its structural integrity and requires replacement
Note on C145: Assumes underground system. For surface runoff system, apply to "Other" category at bottom of form
Note on E145: Catch basins have lost their integrity or are out of alignment. Remove catch basin, reset, and realign
Note on G145: Storm sewer piping is dysfunctional or damaged. Remove and replace.
Note on I145: Detention/retention has failed, but piping and catch basins are functional. Replace detention / retention system
Note on K145: The entire underground system has failed and requires removal and replacement of all components
Note on K146: A portion of the line has lost its structural integrity and requires replacement
Note on K147: A portion of the line has lost its structural integrity and requires replacement
Note on C148: Natural gas lines
Note on K148: A portion of the line has lost its structural integrity and requires replacement
Note on D151: Assumes the private portion of the service lines typically underground after the meter or transformer
Note on I151: The transformer no longer functions and is in need of replacement
Note on K151: The service has failed and is beyond repair or is undersized requiring replacement of transformer and service lines
Note on E152: The generator needs to be tuned up
Note on G152: The valves or other engine parts need to be repaired or replaced and then a tune up
Note on I152: Generator is non-functional or under-sized
Note on K152: The system (generator, tank, services lines connected lighting system) is non-functional or under-sized
Note on G153: The fixtures are nonfunctional and require replacement
Note on K153: The fixtures, supports, and underground wiring need to be replaced
Note on C154: Assumes low voltage lines underground
Note on K154: Site cabling is inadequate or service is interrupted - replace cabling

## Building Type Budget-READ ONLY
Budgeted Replacement Cost of Buildings by Type
Type | Raw Budget / SF (as of 7/1/16) | Inflated Based on State Rate | Developed Budget* | Forwarded RCI Budget
Elementary School | 275 | 302.5 | 417.45 | 417.45
Middle School | 290 | 319 | 440.22 | 0 | NOTE;
K-8 School | 285 | 313.5 | 432.63 | 0 | These are building only costs and any sitework should be added if required
High School | 310 | 341 | 470.58 | 0
Gymnasium Building | 260 | 286 | 394.68 | 0
Pool Building | 350 | 385 | 531.3 | 0
Vocational Building | 300 | 330 | 455.4 | 0
Administrative Building | 300 | 330 | 455.4 | 0
Maintenance Building | 220 | 242 | 333.96 | 0
Storage Building | 200 | 220 | 303.6 | 0
Warehouse | 185 | 203.5 | 280.83 | 0
Food Services Building | 375 | 412.5 | 569.25 | 0
Bus Shelter | 165 | 181.5 | 250.47 | 0
Bus Garage | 185 | 203.5 | 280.83 | 0
Athletic Grandstand | 400 | 440 | 607.2 | 0
Large Greenhouse | 125 | 137.5 | 189.75 | 0
Other Commercial | 230 | 253 | 349.14 | 0
|  |  | RCI Reference | 417.45
*Developed Budget is based on State Assigned factor on PSA Cost Table Sheet
Note:
Small support out buildings shall be assessed as "other" under the primary building assessment and not as their own building assessment
Assumed raw budgets are extrapolated from RLB Cost Estimating Guide and recent public bid results

## County Cost Factor - READ ONLY
County Cost Factor for Physical Assessment Budget Calculation
Counties | Prevailing Wage Rate Regions | Cost Factor | Forwarded Factor
Clatsop | 1 | 1.05 | 0
Columbia | 1 | 1.05 | 0
Tillamook | 1 | 1.05 | 0
Clackamas | 2 | 1.13 | 0
Multnomah | 2 | 1.13 | 0
Washington | 2 | 1.13 | 0
Marion | 3 | 1 | 0
Polk | 3 | 1 | 0
Yamhill | 3 | 1 | 0
Benton | 4 | 1 | 0
Lincoln | 4 | 1 | 1
Linn | 4 | 1 | 0
Lane | 5 | 1 | 0
Douglas | 6 | 0.97 | 0
Coos | 7 | 0.97 | 0
Curry | 7 | 0.97 | 0
Jackson | 8 | 0.97 | 0
Josephine | 8 | 0.97 | 0
Hood River | 9 | 1.05 | 0
Sherman | 9 | 1.05 | 0
Wasco | 9 | 1.05 | 0
Crook | 10 | 0.95 | 0
Deschutes | 10 | 0.95 | 0
Jefferson | 10 | 0.95 | 0
Klamath | 11 | 0.93 | 0
Lake | 11 | 0.93 | 0
Gilliam | 12 | 0.99 | 0
Grant | 12 | 0.99 | 0
Morrow | 12 | 0.99 | 0
Umatilla | 12 | 0.99 | 0
Wheeler | 12 | 0.99 | 0
Baker | 13 | 0.99 | 0
Union | 13 | 0.99 | 0
Wallowa | 13 | 0.99 | 0
Harney | 14 | 0.89 | 0
Malheur | 14 | 0.89 | 0
|  | Selected Factor | 1
NOTES
Regions established by the State of Oregon BOLI Office
Relational rates between regions extrapolated from 2015 National Building Cost Manual (2015)

## Renovations, Additions & Prtbls
A RENOVATIONS
Renovation Number | Date | Construction Type | Square Footage | Usage
B ADDITIONS
Addition Number | Date | Construction Type | Square Footage | Usage
C PORTABLE CLASSROOMS
Portable Number | Date Placed on Site | Age of Portable | Square Footage | Notes

## Security
SCHOOL SAFETY AUDIT ASSESSMENT
| YES | NO | N/A | COMMENTS
School grounds are fenced.
There is one clearly marked and designated entrance for visitors
Signs are posted for visitors to report to main office through a designated entrance.
Restricted areas are clearly marked
Shrubs and foliage are trimmed to allow for good line of sight. (3'-0"/8'- 0" rule)
Shrubs near building have been trimmed "up" to allow view of bottom of building
Bus loading and drop-off zones are clearly defined.
There is a schedule for maintenance of:
a. Outside lights
b. Locks/Hardware
c. Storage Sheds
d. Windows
e. Other exterior buildings
Parent drop-off and pick-up area is clearly defined.
There is adequate lighting around the building.
Lighting is provided at entrances and other points of possible intrusion.
The school ground is free from trash or debris.
The school is free of graffiti.
Play areas are fenced.
Playground equipment has tamper-proof fasteners
Visual surveillance of bicycle racks from main office is possible.
Visual surveillance of parking lots from main office is possible
Parking lot is lighted properly and all lights are functioning
Accessible lenses are protected by some unbreakable material
Staff and visitor parking has been designated
Outside hardware has been removed from all doors except at points of entry.
Ground floor windows:
a. have no broken panes;
b. locking hardware is in working order.
Basement windows are protected with grill or well cover.
Doors are locked when classrooms are vacant.
High-risk areas are protected by high security locks and an alarm system
a. Main office
b. Cafeteria
c. Computer Labs
d. Industrial Arts rooms
e. Science labs
f. Nurses Office
g. Boiler Room
h. Electrical Rooms
i. Phone line access closet
Unused areas of the school can be closed off during after school activities.
There is two-way communication between the main office and:
a. Classroom
b. Duty stations
c. Re-locatable classrooms
d. Staff and faculty outside building
e. Buses
There is a central alarm system in the school. If yes, briefly describe:
The main entrance is visible from the main office.

## ADA
ADA ASSESSMENT
| YES | NO | N/A | COMMENTS
There is at least 1 route from site arrival points that does not require the use of stairs.
If parking is provided for the public, there are adequate number of accessible spaces provide (1 per 25).
There is at least 1 van accessible parking space among the accessible spaces.
The slope of the accessible parking spaces and access aisles is no steeper than 1:48 in all directions.
The access aisles adjoin an accessible route.
Accessible spaces are identified with a sign that includes the International Symbol of Accessibility.
There are signs reading "van accessible" at van accessible spaces.
If the accessible route crosses a curb, there is a curb ramp.
Ramps are sloped no greater than 1:12.
The main entrance is accessible.
If the main entrance is not accessible, there is an alternative accessible entrance.
The alternative accessible entrance can be used independently and during the same hours as the main entrance.
All inaccessible entrances have signs with the International Symbol of Accessibility indicating the location of the nearest accessible entrance.
The door is equipped with hardware, including locks, that is operable with one hand and does not require tight grasping, pinching, or twisting of the wrist.
The operable parts of the door hardware are no less than 34" and no greater than 48" above the floor or ground surface.
In locker rooms, there is at least one room with a bench.
At least one toilet room is accessible (either one for each sex or one unisex).
There are signs with the International Symbol of Accessibility at inaccessible toilet rooms that give directions to accessible toilet rooms.
There is a route to the accessible toilet room(s) that does not include stairs.
The door is equipped with hardware that is operable with one hand and does not require tight grasping, pinching, or twisting of the wrist.
The operable parts of the door hardware are no less than 34" and no greater than 48" above the floor or ground surface.
The door can be opened easily (5 lbs. maximum force).
Lighting controls are operable with one hand and without tight grasping, pinching, or twisting of the wrist.
Mounted switches are no less than 34" and no greater than 48" above the floor or ground surface.

## IT
Information Technology
| YES | NO | N/A | COMMENTS
1. Connectivity “speed “ to the Facility:
a. 10 Gbps or greater
b. 1 Gbps or greater
c. 100 Mbps or less
d. 10 Mbps or less
e. Less than 10 Mbps
2. Local area network connectivity “speed “ at the individual building level:
a. 10 Gbps or greater
b. 1 Gbps or greater
c. 100 Mbps or less
d. 10 Mbps or less
e. Less than 10 Mbps
3. Wireless Coverage:
a. Facility Wide
b. Secure?
c. Type:
i. AC
ii. N
iii. A/B/G
4. Building cabling:
a. Fiber (to the desktop)
b. CAT 6
c. CAT 5 E
d. CAT 5
5. Security:
a. Access control
b. Video Surveillance
c. Central Communications Systems

## Harmful Substances
HARMFUL SUBSTANCES ASSESSMENT
| YES | NO | N/A | COMMENTS
Lead
Has your facility been assessed for lead? If so when?
Is there lead in your facility?
Is lead abatement included in your future bond plans?
Asbestos
Has your facility been assessed for asbestos? If so when?
Is there asbestos in your facility?
Is asbestos abatement included in your future bond plans?
Mold
Has your facility been assessed for mold? If so when?
Is there mold in your facility?
Is mold abatement included in your future bond plans?
Water Quality
Has your facility been assessed for water quality (lead, etc)? If so when?
Is there a water quality concern in your facility?
Is water treatment included in your future bond plans?
PCBs
Has your facility been assessed for PCBs? If so when?
Are there PCBs in your facility?
Is PCB abatement included in your future bond plans?
Radon
Has your facility been assessed for Radon? If so when?
Is there Radon in your facility?
Is Radon management included in your future bond plans?

## IAQ
INDOOR AIR QUALITY ASSESSMENT
| YES | NO | N/A | COMMENTS
Is someone designated to develop and implement an indoor air quality management plan for your school district?
Does your district have an indoor air quality management plan that includes steps for preventing and resolving indoor air quality problems?
Are school buildings inspected once or twice each year for conditions that may lead to indoor air quality problems?
Is a preventive maintenance schedule established and in operation for the heating, ventilation, and air conditioning (HVAC) system? Is the schedule in accordance with the manufacturer's recommendations or accepted practice for the HVAC system?
Does the HVAC preventive maintenance schedule include the following?: checking and/or changing air filters and belts, lubricating equipment parts, checking the motors, and confirming that all equipment is in operating order.
Is the maintenance schedule updated to show all maintenance performed on the building systems?
Does the maintenance schedule include the dates that the building systems maintenance was performed and the names of the persons or companies performing the work?
Are maintenance schedules retained for at least three years?
Are damaged or inoperable components of the HVAC system replaced or repaired as appropriate?
Are reservoirs or parts of the HVAC system with standing water checked visually for microbial growth?
Are water leaks that could promote growth of biologic agents promptly repaired?
Are damp or wet materials that could promote growth of biologic agents promptly dried, replaced, removed, or cleaned?
Are microbial contaminants removed from ductwork, humidifiers, other HVAC and building system components, and from building surfaces such as carpeting and ceiling tiles when found during regular or emergency maintenance activities or visual inspection?
Is general or local exhaust ventilation used where housekeeping and maintenance activities could reasonably be expected to result in exposure to hazardous substances above applicable exposure limits?
Does the HVAC system have CO2 monitoring capability (demand control ventilation)?
Are humidity levels maintained between 30% to 60% relative humidity?
When a contaminant is identified in the make-up air supply, is the source of the contaminant eliminated, or are the make-up inlets or exhaust air outlets relocated to avoid entry of the contaminant into the air system?
If buildings do not have mechanical ventilation, are windows, doors, vents, stacks, and other portals used for natural ventilation operating properly?

## County Names (hidden)
Baker
Benton
Clackamas
Clatsop
Columbia
Coos
Crook
Curry
Deschutes
Douglas
Gilliam
Grant
Harney
Hood River
Jackson
Jefferson
Josephine
Klamath
Lake
Lane
Lincoln
Linn
Malheur
Marion
Morrow
Multnomah
Polk
Sherman
Tillamook
Umatilla
Union
Wallowa
Wasco
Washington
Wheeler
Yamhill

## District Names (hidden)
Institutions_Id | District
2063 | Adel SD 21
2113 | Adrian SD 61
1899 | Alsea SD 7J
2252 | Amity SD 4J
2111 | Annex SD 29
2005 | Arlington SD 3
2115 | Arock SD 81
2041 | Ashland SD 5
2051 | Ashwood SD 8
1933 | Astoria SD 1
2208 | Athena-Weston SD 29RJ
1894 | Baker SD 5J
1969 | Bandon SD 54
2240 | Banks SD 13
2243 | Beaverton SD 48J
1976 | Bend-LaPine Administrative SD 1
2088 | Bethel SD 52
2095 | Blachly SD 90
2052 | Black Butte SD 41
1974 | Brookings-Harbor SD 17C
1896 | Burnt River SD 30J
2046 | Butte Falls SD 91
1995 | Camas Valley SD 21J
1929 | Canby SD 86
2139 | Cascade SD 5
2185 | Centennial SD 28J
1972 | Central Curry SD 1
2105 | Central Linn SD 552
2042 | Central Point SD 6
2191 | Central SD 13J
1945 | Clatskanie SD 6J
1927 | Colton SD 53
2006 | Condon SD 25J
1965 | Coos Bay SD 9
1964 | Coquille SD 8
2186 | Corbett SD 39
1901 | Corvallis SD 509J
2216 | Cove SD 15
2086 | Creswell SD 40
1970 | Crook County SD
2089 | Crow-Applegate-Lorane SD 66
2050 | Culver SD 4
2190 | Dallas SD 2
2187 | David Douglas SD 40
2253 | Dayton SD 8
2011 | Dayville SD 16J
2017 | Diamond SD 7
2021 | Double O SD 28
1993 | Douglas County SD 15
1991 | Douglas County SD 4
2019 | Drewsey SD 13
2229 | Dufur SD 29
2043 | Eagle Point SD 9
2203 | Echo SD 5
2217 | Elgin SD 23
1998 | Elkton SD 34
2221 | Enterprise SD 21
1930 | Estacada SD 108
2082 | Eugene SD 4J
2193 | Falls City SD 57
2084 | Fern Ridge SD 28J
2241 | Forest Grove SD 15
2248 | Fossil SD 21J
2020 | Frenchglen SD 16
2245 | Gaston SD 511J
2137 | Gervais SD 1
1931 | Gladstone SD 115
2000 | Glendale SD 77
1992 | Glide SD 12
2054 | Grants Pass SD 7
2100 | Greater Albany Public SD 8J
2183 | Gresham-Barlow SD 10J
2014 | Harney County SD 3
2015 | Harney County SD 4
2023 | Harney County Union High SD 1J
2114 | Harper SD 66
2099 | Harrisburg SD 7J
2201 | Helix SD 1
2206 | Hermiston SD 8
2239 | Hillsboro SD 1J
2024 | Hood River County SD
1895 | Huntington SD 16J
2215 | Imbler SD 11
3997 | Ione SD R2
2053 | Jefferson County SD 509J
2140 | Jefferson SD 14J
1934 | Jewell SD 8
2008 | John Day SD 3
2107 | Jordan Valley SD 3
2219 | Joseph SD 6
2091 | Junction City SD 69
2109 | Juntura SD 12
2057 | Klamath County SD
2056 | Klamath Falls City Schools
2262 | Knappa SD 4
2212 | La Grande SD 1
2059 | Lake County SD 7
1923 | Lake Oswego SD 7J
2101 | Lebanon Community SD 9
2097 | Lincoln County SD
2012 | Long Creek SD 17
2092 | Lowell SD 71
2112 | Malheur County SD 51
2085 | Mapleton SD 32
2094 | Marcola SD 79J
2090 | McKenzie SD 68
2256 | McMinnville SD 40
2048 | Medford SD 549C
2205 | Milton-Freewater Unified SD 7
2249 | Mitchell SD 55
1925 | Molalla River SD 35
1898 | Monroe SD 1J
2010 | Monument SD 8
2147 | Morrow SD 1
2145 | Mt Angel SD 91
1968 | Myrtle Point SD 41
2198 | Neah-Kah-Nie SD 56
2199 | Nestucca Valley SD 101J
2254 | Newberg SD 29J
1966 | North Bend SD 13
1924 | North Clackamas SD 12
1996 | North Douglas SD 22
2061 | North Lake SD 14
2141 | North Marion SD 15
2214 | North Powder SD 8J
2143 | North Santiam SD 29J
4131 | North Wasco County SD 21
2110 | Nyssa SD 26
1990 | Oakland SD 1
2093 | Oakridge SD 76
2108 | Ontario SD 8C
1928 | Oregon City SD 62
1926 | Oregon Trail SD 46
2060 | Paisley SD 11
2181 | Parkrose SD 3
2207 | Pendleton SD 16
2192 | Perrydale SD 21
1900 | Philomath SD 17J
2039 | Phoenix-Talent SD 4
2202 | Pilot Rock SD 2
2016 | Pine Creek SD 5
1897 | Pine Eagle SD 61
2047 | Pinehurst SD 94
2081 | Pleasant Hill SD 1
2062 | Plush SD 18
1973 | Port Orford-Langlois SD 2CJ
2180 | Portland SD 1J
1967 | Powers SD 31
2009 | Prairie City SD 4
2045 | Prospect SD 59
1946 | Rainier SD 13
1977 | Redmond SD 2J
2001 | Reedsport SD 105
2182 | Reynolds SD 7
1999 | Riddle SD 70
2188 | Riverdale SD 51J
2044 | Rogue River SD 35
2142 | Salem-Keizer SD 24J
2104 | Santiam Canyon SD 129J
1944 | Scappoose SD 1J
2103 | Scio SD 95
1935 | Seaside SD 10
2257 | Sheridan SD 48J
2195 | Sherman County SD
2244 | Sherwood SD 88J
2138 | Silver Falls SD 4J
1978 | Sisters SD 6
2096 | Siuslaw SD 97J
2022 | South Harney SD 33
2087 | South Lane SD 45J3
1994 | South Umpqua SD 19
2225 | South Wasco County SD 1
2247 | Spray SD 1
2083 | Springfield SD 19
1948 | St Helens SD 502
2144 | St Paul SD 45
2209 | Stanfield SD 61
2018 | Suntex SD 10
2003 | Sutherlin SD 130
2102 | Sweet Home SD 55
2055 | Three Rivers/Josephine County SD
2242 | Tigard-Tualatin SD 23J
2197 | Tillamook SD 9
2222 | Troy SD 54
2210 | Ukiah SD 80R
2204 | Umatilla SD 6R
2213 | Union SD 5
2116 | Vale SD 84
1947 | Vernonia SD 47J
2220 | Wallowa SD 12
1936 | Warrenton-Hammond SD 30
1922 | West Linn-Wilsonville SD 3J
2255 | Willamina SD 30J
2002 | Winston-Dillard SD 116
2146 | Woodburn SD 103
2251 | Yamhill Carlton SD 1
1997 | Yoncalla SD 32

## Physical Assessment Comments
Cell: C10
Comment: Standard spread and strip / perimeter footings; Apply rates to bldg footprint area
Cell: H10
Comment: Minor cracking observed ‐ fill and seal the cracks to prevent water intrusion
Cell: L10
Comment: Settlement observed in surrounding conditions ‐ requiring stabilization of the foundation, sub‐grade adjustment, and re‐enforcement of the foundation
Cell: C11
Comment: Pilings or other extended foundation systems that overcome non‐standard soil conditions; Apply rates to bldg footprint area
Cell: H11
Comment: Minor cracking observed ‐ fill and seal the cracks to prevent water intrusion
Cell: L11
Comment: Settlement observed in surrounding conditions ‐ requiring stabilization of the foundation, sub‐grade adjustment, and re‐enforcement of the foundation
Cell: C12
Comment: Standard ground‐set concrete slab. If slab is elevated (i.e. has a crawl space or basement), apply conditions to B1010 instead; Apply rates to bldg footprint area
Cell: J12
Comment: Separation cracks occurring requiring route and fill and patch
Cell: L12
Comment: Differential settlement occurring ‐ requires removal of section of slab, adjustment to sub‐grade, and new infill
Cell: C15
Comment: Assumed as concrete walls with water‐proofing on the exterior. Includes only the structural portion and not the wall finishes; Apply to wall surface area
Cell: H15
Comment: Inadequate below grade venting is observed ‐ cut in and add venting
Cell: J15
Comment: Wall is cracked and spalling requiring route and fill and patch and re‐finish
Cell: L15
Comment: Wall is cracked with evidence of water intrusion. Repairs to be implemented and water barrier to be applied to be applied
Cell: C18
Comment: A suspended floor including the structural members and floor construction, but not including the actual finish
Cell: J18
Comment: Deck lifting, settling, or uneven ‐ appears related to the deck itself and not the structural support below ‐ requires removal and replacement of deck
Cell: N18
Comment: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Cell: J19
Comment: Deck lifting, settling, or uneven ‐ appears related to the deck itself and not the structural support below ‐ requires removal and replacement of deck
Cell: N19
Comment: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Cell: J20
Comment: Deck lifting, settling, or uneven ‐ appears related to the deck itself and not the structural support below ‐ requires removal and replacement of deck
Cell: N20
Comment: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Cell: C21
Comment: The roof structure referring to the supporting structure and the deck but excluding the roofing itself
Cell: L21
Comment: Evidence of a spongy decking from water intrusion ‐ replacing the deck but not the trusses
Cell: N21
Comment: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Cell: L22
Comment: Evidence of a flexing decking from water intrusion / rust ‐ replacing the deck but not the trusses
Cell: N22
Comment: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Cell: L23
Comment: Evidence of a spongy / spalling deck from water intrusion ‐ replacing the deck but not the beams
Cell: N23
Comment: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Cell: D25
Comment: Apply to wall surface area
Cell: J25
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: L25
Comment: Cracks visible ‐ route and patch prior to painting
Cell: D26
Comment: Apply to wall surface area
Cell: J26
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: L26
Comment: Some blocks are damaged, needing patch and repair prior to sealing or painting
Cell: N26
Comment: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Cell: D27
Comment: Apply to wall surface area
Cell: J27
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: L27
Comment: A number of panels are damaged, requiring patch and repair prior to re‐painting
Cell: N27
Comment: The panels are lifting or separating or otherwise losing their integrity ‐ remove and replace
Cell: D28
Comment: Apply to wall surface area
Cell: J28
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: L28
Comment: Cracks visible ‐ route and patch prior to painting
Cell: N28
Comment: System in failure with evidence of water intrusion ‐ remove and replace
Cell: D29
Comment: Apply to wall surface area
Cell: J29
Comment: Minor repairs needed to mortar, prep, and re‐sealing
Cell: L29
Comment: Mortar missing in a majority of areas requiring complete re‐pointing and sealing
Cell: N29
Comment: Masonry visibly damaged and requiring removal and replacement
Cell: D30
Comment: Apply to glazed area
Cell: J30
Comment: The glazing is double pane but is broken or fogged and requires replacement
Cell: L30
Comment: The glazing is single pane or the sash is damaged ‐ either requires replacement of the sash and its glazing
Cell: N30
Comment: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Cell: D31
Comment: This assumes both individual aluminum windows and storefront systems; Apply to glazed area
Cell: J31
Comment: The glazing is double pane but is broken or fogged and requires replacement
Cell: L31
Comment: The glazing is single pane or the sash is damaged ‐ either requires replacement of the sash and its glazing
Cell: N31
Comment: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Cell: D32
Comment: This assumes a metal windows system clad with wood or vinyl; Apply to glazed area
Cell: J32
Comment: The glazing is double pane but is broken or fogged and requires replacement
Cell: L32
Comment: The glazing is single pane or the sash is damaged ‐ either requires replacement of the sash and its glazing
Cell: N32
Comment: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Cell: D33
Comment: Apply to glazed area
Cell: J33
Comment: Minor leaks at wall seams ‐ re‐caulk and re‐seal
Cell: L33
Comment: Window panels fogged and require replacement
Cell: N33
Comment: Settlement or displacement is evident
Cell: D34
Comment: Apply to door count
Cell: J34
Comment: Door hardware is damaged or non‐functional and requires replacement
Cell: L34
Comment: Door panel and hardware are damaged and require replacement
Cell: N34
Comment: Door frame, door, and hardware are damaged and require replacement
Cell: D35
Comment: Apply to door count
Cell: J35
Comment: Door hardware is damaged or non‐functional and requires replacement
Cell: L35
Comment: Door panel and hardware are damaged and require replacement
Cell: N35
Comment: Door frame, door, and hardware are damaged and require replacement
Cell: D36
Comment: Apply to door count
Cell: J36
Comment: Door hardware is damaged or non‐functional and requires replacement
Cell: L36
Comment: Door panel and hardware are damaged and require replacement
Cell: N36
Comment: Door frame, door, and hardware are damaged and require replacement
Cell: C38
Comment: Assumes the insulation, roof covering, and associated flashings, gutters, and downspouts
Cell: D38
Comment: Apply to roof area
Cell: H38
Comment: Small number of shingles lifting and/or separation in a portion of flashing
Cell: J38
Comment: Leaks in a specific area or zone related to poor detailing and or flashing
Cell: L38
Comment: System in complete failure with multiple leaks and multiple examples of visible breaches in system ‐ Replace roof system OVER TOP OF EXISTING
Cell: N38
Comment: System in complete failure with multiple leaks and multiple examples of visible breaches in system ‐ REMOVE AND Replace roof system
Cell: D39
Comment: Apply to roof area
Cell: H39
Comment: Minor blistering requiring isolated patches
Cell: J39
Comment: Leaks in a specific area or zone related to poor detailing and or flashing or unchecked blisters
Cell: L39
Comment: System in complete failure with multiple leaks and multiple examples of visible breaches in system ‐ Replace roof system OVER TOP OF EXISTING
Cell: N39
Comment: System in complete failure with multiple leaks and multiple examples of visible breaches in system ‐ REMOVE AND Replace roof system
Cell: D40
Comment: Apply to roof area
Cell: H40
Comment: Minor blistering requiring isolated patches
Cell: J40
Comment: Leaks in a specific area or zone related to poor detailing and or flashing or seam separation
Cell: L40
Comment: System in complete failure with multiple leaks and multiple examples of visible breaches in system ‐ Prep and re‐coat roof system OVER TOP OF EXISTING
Cell: N40
Comment: System in complete failure with multiple leaks and multiple examples of visible breaches in system ‐ REMOVE AND Replace roof system
Cell: D41
Comment: Apply to roof area
Cell: J41
Comment: Leaks are occurring and flashing at seams or transitions has separated requiring replacement of flashing and sealant
Cell: N41
Comment: Panels have lifted or separated and water intrusion is evident. Remove and replace panels and associated flashing
Cell: D42
Comment: Apply to roof area
Cell: J42
Comment: Leaks occurring at isolated areas requiring grout removal and re‐grout at isolated tile locations
Cell: N42
Comment: Tiles are cracked, loose, or damaged and require removal and replacement
Cell: D43
Comment: Apply to roof opening area
Cell: J43
Comment: Minor leaking is occurring, requiring re‐caulk and re‐seal
Cell: N43
Comment: The panes or framing are damaged beyond repair and requires replacement
Cell: D44
Comment: Apply to roof opening area
Cell: N44
Comment: The door is non‐functional or damaged beyond repair and requires replacement
Cell: D47
Comment: Apply to wall surface area
Cell: N47
Comment: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Cell: D48
Comment: Apply to wall surface area
Cell: L48
Comment: There are some blocks that are damaged and requires a strategic removal and replacement
Cell: N48
Comment: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Cell: D49
Comment: Apply to door count
Cell: J49
Comment: Door hardware is damaged or non‐functional and requires replacement
Cell: L49
Comment: Door panel and hardware are damaged and require replacement
Cell: N49
Comment: Door frame, door, and hardware are damaged and require replacement
Cell: D50
Comment: Apply to door count
Cell: J50
Comment: Door hardware is damaged or non‐functional and requires replacement
Cell: L50
Comment: Door panel and hardware are damaged and require replacement
Cell: N50
Comment: Door frame, door, and hardware are damaged and require replacement
Cell: D53
Comment: Apply to stair flights
Cell: L53
Comment: Rails not compliant with code and require removal and replacement
Cell: N53
Comment: Structural integrity of stair unit is compromised and requires its removal and replacement
Cell: D54
Comment: Apply to stair flights
Cell: H54
Comment: Rust visible ‐ prep and re‐finish
Cell: L54
Comment: Rails not compliant with code and require removal and replacement
Comment: Structural integrity of stair unit is compromised and requires its removal and replacement
Cell: D55
Comment: Apply to stair flights
Cell: L55
Comment: An isolated structural crack or separation requiring re‐enforcement in place
Cell: N55
Comment: Structural cracking and separation occurring in multiple locations ‐ remove and replace the stair unit
Cell: D56
Comment: Apply stair tread and riser area
Cell: H56
Comment: Surface feels rough and/or taking in moisture from the surface resulting in staining ‐ prep and re‐seal
Cell: N56
Comment: Severe cracking requiring removal and replacement of tread in fills
Cell: D57
Comment: Apply stair tread and riser area
Cell: N57
Comment: finish is lifting or separating and creating trip hazards ‐ remove and replace
Cell: D59
Comment: Apply to surface treated
Cell: H59
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: N59
Comment: Systemic failure of finish, possible water intrusion ‐ requires removal and replacement
Cell: D60
Comment: Apply to surface treated
Cell: H60
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: J60
Comment: Surface is damaged ‐ patching of the surface is required prior to painting
Cell: N60
Comment: Systemic failure of finish, possible water intrusion ‐ requires removal and replacement
Cell: D61
Comment: Apply to surface treated
Cell: H61
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: N61
Comment: Systemic failure of finish, possible water intrusion ‐ requires removal and replacement
Cell: D62
Comment: Apply to surface treated
Cell: H62
Comment: Grout is damaged or deteriorated
Cell: N62
Comment: Tiles are cracked or in disrepair
Cell: D63
Comment: Apply to surface treated
Cell: N63
Comment: worn or severely stained or starting to pull up / bubble
Cell: D64
Comment: Apply to surface treated
Cell: H64
Comment: sporadic number of tiles are lifting or cracked / broken and require replacement
Cell: L64
Comment: The majority of tiles are lifting, cracking / broken and require replacement ‐ the tiles or glue are NOT asbestos
Cell: N64
Comment: The majority of tiles are lifting, cracking / broken and require replacement ‐ the tiles or glue are asbestos
Cell: D65
Comment: Apply to surface treated
Cell: N65
Comment: Severely worn or seams separating ‐ replace
Cell: D66
Comment: Apply to surface treated
Cell: H66
Comment: Surface feels rough and/or taking in moisture from the surface resulting in staining ‐ prep and re‐seal
Cell: N66
Comment: Significant cracking, but not differential ‐ requires prep and crack filling prior to re‐seal. If differential, refer to slab on grade of floor construction above
Cell: D67
Comment: Apply to surface treated
Cell: H67
Comment: Grout is damaged or deteriorated
Comment: Tiles are cracked or in disrepair
Cell: D68
Comment: Apply to surface treated
Cell: N68
Comment: Systemic blistering or severely worn traffic areas ‐ strip and replace
Cell: D69
Comment: Apply to surface treated
Cell: J69
Comment: Surface is damaged ‐ requires sanding, repair, and re‐coat / re‐stripe
Cell: N69
Comment: Wood planks are deteriorated, separating, and multiple dead spots ‐ replace floor
Cell: D70
Comment: Apply to surface treated
Cell: H70
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: J70
Comment: Surface is damaged ‐ patching of the surface is required prior to painting
Cell: N70
Comment: Systemic failure of finish, possible water intrusion ‐ requires removal and replacement
Cell: D71
Comment: Apply to surface treated
Cell: H71
Comment: Stained or damaged ceiling tiles
Cell: J71
Comment: Diagonal bracing missing from grid
Cell: N71
Comment: Grid is sagging with tiles compromised ‐ requires replacement of system
Cell: D72
Comment: Apply to surface treated
Cell: H72
Comment: Stained or damaged ceiling tiles
Cell: N72
Comment: Systemic failure of finish, possible water intrusion ‐ requires removal and replacement
Cell: D73
Comment: Apply to surface treated
Cell: N73
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: C76
Comment: Assume standard cab‐style elevator; Apply per stop
Cell: E76
Comment: Insert number of elevators * number of stories ‐ i.e. if there are 2 elevators each going 3 stories ‐ insert 6
Cell: H76
Comment: The elevator doors are damaged and require replacement
Cell: J76
Comment: Electrical components are not working
Cell: L76
Comment: Replacement of the hoist cables, guide rails, or other similar mechanical components is required
Cell: N76
Comment: Mechanical and electrical components have deteriorated requiring the replacement of the system
Cell: C77 Comment: Apply per flight
Cell: E77
Comment: Insert number of escalators * number of stories ‐ i.e. if there are 2 escalators each going 3 stories ‐ insert 6
Cell: J77
Comment: Electrical components are not working
Cell: N77
Comment: Mechanical and electrical components have deteriorated requiring the replacement of the system
Cell: C78
Comment: Assume open vertical or inclined lift; Apply per unit
Cell: E78
Comment: Insert number of lifts
Cell: J78
Comment: Electrical components are not working
Cell: N78
Comment: Mechanical and electrical components have deteriorated requiring the replacement of the system
Cell: C80
Comment: All fixtures (toilets, urinals, sinks, showers, etc.) to be lumped together here
Cell: J80
Comment: Flush valves or faucets are non‐functional and require replacement
Cell: N80
Comment: The fixture itself is broken or is not compliant with water efficiency standards
Cell: H81
Comment: The vale stems, pressure gauges, and gate valves no longer function.
Cell: J81
Comment: The insulation on the piping is in disrepair, loose, or missing.
Cell: N81
Comment: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Cell: H82
Comment: In some areas, there are back ups requiring the replacement of the broken floor or wall, clean outs, routing and cleaning the problem areas, and snaking floor drains
Cell: N82
Comment: The runs and risers are deteriorated, displaced, or have systemic leaks and requires full replacement
Cell: C83
Comment: This is for the presence of interior rain drains; note building percentage based on area of roof served ‐ excludes external downspouts
Cell: J83
Comment: The rain drain or overflow is damaged and needs replacement
Cell: N83
Comment: The integrity of the piping is compromised and is leaking inside the walls
Cell: C86
Comment: This assumes gas piping
Cell: H86
Comment: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Cell: N86
Comment: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Cell: H87
Comment: The burner is inefficient and requires refurbishment
Cell: J87
Comment: One major component needs to be replaced
Cell: L87
Comment: More than one major component needs to be replaced
Cell: N87
Comment: The system is in failure
Cell: L88
Comment: Some of the distribution fans and coils are dysfunctional.
Cell: N88
Comment: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Cell: J89
Comment: A small number of minor parts need to be repaired or replaced
Cell: L89
Comment: The burner, combustion chamber, or fan are faulty and require replacement
Cell: N89
Comment: The entire furnace requires replacement
Cell: J90
Comment: A small number of minor parts need to be repaired or replaced
Cell: L90
Comment: System operating at low efficiency; shell exhibits corrosion. Retube heat exchanger
Cell: N90
Comment: System operates at low efficiency with corrosion and leaks apparent. Replace system
Cell: L91
Comment: Some of the distribution fans and coils are dysfunctional.
Cell: N91
Comment: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Cell: N92
Comment: The chiller is beyond economic repair
Cell: J93
Comment: Dampers in the system are inoperative
Cell: L93
Comment: The insulation is damaged or missing
Cell: N93
Comment: The ductwork is damaged or inadequately designed and requires replacement
Cell: H94
Comment: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Cell: J94
Comment: The insulation on the piping is in disrepair, loose, or missing.
Cell: N94
Comment: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Cell: N95
Comment: Entire unit is failing to function
Cell: J96
Comment: Internal compressor is bad and requires replacement
Cell: N96
Comment: Entire unit is failing to function
Cell: H97
Comment: In‐room valve is failing and requires replacement
Cell: N97
Comment: Entire unit is failing to function
Cell: L98
Comment: Some of the sensors or valve actuators are dysfunctional. Replace these sensors or actuators
Cell: N98
Comment: The majority of sensors or actuators are faulty, and the system software is dysfunctional OR the system is an older / obsolete pneumatic system ‐ replace
Cell: N99
Comment: One or more zones require re‐balancing
Cell: J102
Comment: Sprinkler heads are inoperable or non‐compliant and need to be replaced
Cell: N102
Comment: The piping has deteriorated or clogged or is non‐compliant and needs to be replaced, including heads
Cell: J103
Comment: The Siamese twin connection, tamper flow switches, or flow control valves are inoperable and need to be replaced
Cell: N103
Comment: The fire pump is beyond repair and needs to be replaced
Cell: C104
Comment: Assume chemical extinguishing system
Cell: J104
Comment: The back‐up tank has been discharged or lacks pressure and needs to be replaced
Cell: N104
Comment: The system is non‐functional or not compliant with the current needs and needs to be replaced
Cell: J107
Comment: Wiring has systemic problems or does not meet code and needs to be replaced
Cell: L107
Comment: Branch panels are obsolete with replacement breakers difficult to acquire and requires replacement
Comment: Main switchgear is obsolete or undersized and requires replacement, including service into building
Cell: L108
Comment: The lighting fixtures are obsolete or non‐functional and require replacement
Cell: N108
Comment: Replacement of fixtures is requiring the replacement of the wiring as well ‐ includes fixtures AND wiring
Cell: J109
Comment: There are individual devices that are not functional.
Cell: L109
Comment: The master control panel is obsolete or not functional
Cell: N109
Comment: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Cell: J110
Comment: There are individual devices that are not functional.
Cell: L110
Comment: The master control panel is obsolete or not functional
Cell: N110
Comment: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Cell: J111
Comment: There are individual devices that are not functional.
Cell: L111
Comment: The master control panel is obsolete or not functional
Cell: N111
Comment: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Cell: J112
Comment: There are individual devices that are not functional.
Cell: L112
Comment: The master control panel is obsolete or not functional
Cell: N112
Comment: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Cell: J113
Comment: There are individual devices that are not functional.
Cell: L113
Comment: The master control panel is obsolete or not functional
Cell: N113
Comment: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Cell: J114
Comment: There are individual devices that are not functional or in regular alarm
Cell: L114
Comment: The master control panel is obsolete or not functional
Cell: N114
Comment: The entire system is dysfunctional and constantly in trouble mode with areas not fully covered. Remove and replace system
Cell: H115
Comment: Individual room sensors are failing and require replacement
Cell: L115
Comment: The central control panel and software need upgraded
Cell: N115
Comment: The entire system is in failure and requires replacement of sensors, wiring and central panel
Cell: H120
Comment: 2‐3 pieces of equipment require replacement
Cell: J120
Comment: Counters and sinks are not code compliant and require replacement with stainless steel and sink system
Cell: L120
Comment: Walk‐in cooler and freezer are not functional or function intermittently and require replacement
Cell: N120
Comment: Walk‐ins and kitchen design does not meet current functional requirements or has become obsolete and requires complete replacement as a full prep kitchen
Cell: H121
Comment: 2‐3 pieces of equipment require replacement
Cell: L121
Comment: Mechanical and electrical service upgrades are required to meet code and amount of program equipment
Cell: N121
Comment: Both mechanical and electrical AND equipment needs replacement to meet program criteria and code
Cell: J122
Comment: Room lacking (and needing) eye wash or fume hood
Cell: L122
Comment: Sinks are in disrepair and require replacement
Comment: Work stations need upgrades to meet current program criteria ‐ replace
Cell: J123
Comment: Storage units damaged or in disrepair
Cell: L123
Comment: Sinks are in disrepair and require replacement
Cell: N123
Comment: Work stations need upgrades to meet current program criteria ‐ replace
Cell: E124
Comment: Insert number of seats
Cell: J124
Comment: Seats damaged and need replacement OR sound OR lighting system inadequate and needs upgraded
Cell: L124
Comment: Fly rigging in disrepair and needs upgrading
Cell: N124
Comment: 2 or more stage system dysfunctional and needs upgrade / replacement to production systems
Cell: H125
Comment: An accessory is damaged or missing
Cell: J125
Comment: Accessories need to be replaced to meet ADA
Cell: L125
Comment: The stall doors are not functional or missing and need to be replaced
Cell: N125
Comment: The restrooms stall structure is failing or needs re‐configuration and needs to be replaced
Cell: D126
Comment: Note anything specific in the "Other" category at the bottom of the assessment form
Cell: C129
Comment: Assume fixed casework (counters, cabinets, shelving, etc.)
Cell: H129
Comment: The counter top or exposed surface has been damaged and can be refinished
Cell: J129
Comment: The drawers and/or doors are damaged and require replacement including hardware
Cell: L129
Comment: A combination of minor and moderate action is required, but the box is still salvageable
Cell: N129
Comment: The casework is severely damaged throughout or is obsolete for the purposes of the space and needs to be replaced
Cell: C130
Comment: Assume loose furnishings (desks, chairs, tables, etc.)
Cell: N130
Comment: The furnishings are severely worn or are inappropriate for the age of students or function of space and require replacement
Cell: C136
Comment: Paved only or needs to be paved; Apply to surface area
Cell: E136
Comment: Indicate SF of road
Cell: H136
Comment: Minor cracking exists and can be resolved with application of a slurry coat
Cell: L136
Comment: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated
Cell: N136
Comment: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over‐ex of sub‐grade with complete replacement. Where there is only a gravel road and a paved one is needed, this category shall be used
Cell: C137
Comment: Paved only or needs to be paved; Apply to surface area
Cell: E137
Comment: Indicate number of stalls
Cell: H137
Comment: Minor cracking exists and can be resolved with application of a slurry coat
Cell: L137
Comment: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated
Cell: N137
Comment: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over‐ex of sub‐grade with complete replacement. Where there is only a gravel lot and a paved one is needed, this category shall be used
Cell: C138
Comment: Concrete only or needs to be concrete; Apply to surface area
Cell: E138
Comment: Indicate square footage of walks and plazas
Cell: L138
Comment: Sections are broken with differential settlement requiring the removal of the effected panels and replacement
Cell: N138
Comment: Not only are sections of the concrete broken, but there is evidence of settlement surrounding the walk requiring removal through sub‐grade and replacement. Where there is no concrete walk, but one is needed, this category shall be used
Cell: C139
Comment: Chain‐link fencing; Apply to LF of fence
Cell: E139
Comment: Indicate length of fencing ‐ assuming 6' high chain‐link
Cell: L139
Comment: The fence fabric is damaged and needs to be replaced
Cell: N139
Comment: The fencing has lost its structural integrity and is beyond repair.
Cell: C140
Comment: Irrigation systems. Other landscape or field items should be included in "Other" category at bottom of assessment form; Apply to landscape area
Cell: E140
Comment: Indicate square footage of landscaped area served (including grass areas)
Cell: N140
Comment: Irrigation system is dysfunctional and beyond repair
Cell: D142
Comment: Assumes 4" line to building. Wells should be placed in "Other" category at bottom of form; Apply to surface area
Cell: N142
Comment: A portion of the line has lost its structural integrity and requires replacement
Cell: D143
Comment: Assumes 6" line to building. Wells and holding tanks should be placed in "Other" category at bottom of form; Apply to surface area
Cell: N143
Comment: A portion of the line has lost its structural integrity and requires replacement
Cell: C144
Comment: Lines only. Septic fields, tanks, etc. should be placed in "other" category at bottom of form; Apply to surface area
Cell: N144
Comment: A portion of the line has lost its structural integrity and requires replacement
Cell: C145
Comment: Assumes underground system. For surface runoff system, apply to "Other" category at bottom of form; Apply to surface area
Cell: H145
Comment: Catch basins have lost their integrity or are out of alignment. Remove catch basin, reset, and realign
Cell: J145
Comment: Storm sewer piping is dysfunctional or damaged. Remove and replace.
Cell: L145
Comment: Detention/retention has failed, but piping and catch basins are functional. Replace detention / retention system
Cell: N145
Comment: The entire underground system has failed and requires removal and replacement of all components
Cell: C146
Comment: Apply to surface area
Cell: N146
Comment: A portion of the line has lost its structural integrity and requires replacement
Cell: C147
Comment: Apply to surface area
Cell: N147
Comment: A portion of the line has lost its structural integrity and requires replacement
Cell: C148
Comment: Natural gas lines; Apply to surface area
Cell: N148
Comment: A portion of the line has lost its structural integrity and requires replacement
Cell: D151
Comment: Assumes the private portion of the service lines typically underground after the meter or transformer; Apply to surface area
Cell: L151
Comment: The transformer no longer functions and is in need of replacement
Cell: N151
Comment: The service has failed and is beyond repair or is undersized requiring replacement of transformer and service lines
Cell: D152
Comment: Apply to generator quantity
Cell: H152
Comment: The generator needs to be tuned up
Cell: J152
Comment: The valves or other engine parts need to be repaired or replaced and then a tune up
Cell: L152
Comment: Generator is non‐functional or under‐sized
Cell: N152
Comment: The system (generator, tank, services lines connected lighting system) is non‐functional or under‐sized
Cell: C153
Comment: Apply to surface area
Cell: J153
Comment: The fixtures are nonfunctional and require replacement
Cell: N153
Comment: The fixtures, supports, and underground wiring need to be replaced
Cell: C154
Comment: Assumes low voltage lines underground; Apply to surface area
Cell: N154
Comment: Site cabling is inadequate or service is interrupted ‐ replace cabling
Cell: C158
Comment: For assessment professional to hand enter for specialty items and systems that do not fit into categories above